ON BOREHOLES

MANUAL

P-WASHE

NORTHERN PROVINCE

P-WASHE O&M Task Team – April 2004

TABLE OF CONTENTS

ACTIVITY									       PAGE

1.	INTRODUCTION								    1

1.1.	Objective and content	1

1.2.	Target	1

1.3.	Application	1

2.	DESCRIPTION OF BOREHOLE						    2

2.1.	Borehole structure	2

2.1.1.	Drilling depth	2

2.1.2.	Diameters of boreholes	2

2.1.3.	Casing pipes and well screens:	2

2.1.4.	Gravel packing	2

2.1.5.	Grouting	3

2.1.6.	Centralisers	3

2.2.	Borehole design	3

2.2.1.	Borehole structural design	3

2.3.	Recommended type of lifting device	4

2.4.	Advantages and disadvantages of boreholes	4

3.	SITING OF BOREHOLES							    5

3.1.	Participatory site selection process	5

3.1.1.	Steps in the siting process	5

3.2.	Technical/scientific selection of a site	7

4.	BOREHOLE CONSTRUCTION PROCEDURES			   8

4.1.	General information	8

4.1.1.	Important considerations	8

4.1.2.	Preparatory and initial works	8

4.1.3.	Supervision and monitoring arrangements	9

4.2.	Borehole drilling	9

4.2.1.	Drilling Methods	10

4.2.2.	Drilling plant, equipment, tools etc.	13

4.2.3.	Stratification sampling	15

4.3.	Borehole casing	16

4.4.	Gravel packing and grouting	16

4.5.	Borehole development	17

4.5.1.	Borehole development methods	17

4.6.	Borehole pumping test	18

4.6.1.	Pumping test process	18

4.7.	Water quality analysis	19

4.8.	Water lifting devices	19

4.9.	Run-off water drainage facility / above ground works	20

5.	OPERATION AND MAINTENANCE					  21

5.1.	Preparation for operation and maintenance	21

5.2.	Implementation of o&m	24

5.2.1.	Organisation for implementation of O&M					  24

5.2.2.	Day to day running of the borehole	29

5.2.3.	Maintenance of borehole facility	30

5.2.4.	Resource mobilization for O&M	33

# 5.3.	Trouble Shooting  ……………………………………………………………35

| # LIST OF ABBREVIATIONS AND ACRONYMS |  |
| --- | --- |
| # ABBREVIATION | DESCRIPTION |
| # AIDS | Acquired Immuno Deficiency Syndrome |
| CFM |  |
| DTH | Down The Hole |
| D-WASHE | District Water Sanitation and Health Education |
| ETC | Et cetra |
| FRP | Fibre Reinforced Plastic |
| HIV | Human Immuno-deficiency Virus |
| HRS | Hours |
| I.E. | That is |
| IRC | International Resource Centre |
| KPA | Kilo Pascal |
| L/S | Litres per second |
| M | Metres |
| M&E | Monitoring and Evaluation |
| MM | Millimetres |
| O&M | Operation and Maintenance |
| PHHE | Participatory Health and Hygiene Education |
| PSI | Pressure in Kilograms per Square Inches |
| PVC | Polyvinyl chloroprene |
| P-WASHE | Provincial Water Sanitation and Health Education |
| RWSS | Rural Water Supply and Sanitation |
| SUB DISTRICT WASHE | Sub District Water, Sanitation and Health Education |
| TAZARA | Tanzania – Zambia Railway Authority |
| V-WASHE | Village Water Sanitation and Health Education |
| WASHE | Water, Sanitation and Health Education |
| WHO | World Health Organisation |

| LIST OF FIGURES |  |  |
| --- | --- | --- |
| FIG | DESCRIPTION | PAGE |
| 1 | Cable tool percussion rig tools | 13 |
| 2 | Typical Caretaker selection Criteria | 21 |
| 3 (a) | Initial O&M Tools | 22 |
| 3 (b) | Tool Kit for installation, Reconditioning and Maintenance of India Mark II Deep Well Pump [a. Standard Tools, b. Special Tools] | 22 |
| 4 | Areas of training for Care Takers | 23 |
| 5 | O&M Requirements | 23 |
| 6 | Composition of V-WASHE Committee | 24 |
| 7 | Reporting system for faults | 28 |
| 8 | Some Rules and Guidelines on use of Boreholes | 29 |
| 9 | Minor Repairs | 32 |
| 10 | Major Repairs | 33 |

| # LIST OF TABLES |  |
| --- | --- |
| DESCRIPTION | PAGE |
| Table 1: Drilling Methods | 10 |
| Table 2: Spares for pump – Head, Cylinder and GI riser pipes | 23 |
| Table 3: WASHE structures, Roles/Responsibilities | 25 |
| Table 4: Preventive Maintenance activities | 31 |
| Table 5: Trouble Shooting | 35 |

# ACKNOWLEDGEMENTS

The development of this manual on boreholes involved a series of activities and active participation of officers from Northern province P-WASHE O&M Task Team.

The P-WASHE wishes to most sincerely thank the Task Team for their hard work and commitment shown in the whole process of developing this new manual.

The P-WASHE further extends its gratitude to Development Cooperation Ireland Northern Province Development Programme (NPDP) for the great support rendered in the development of the manual through its technical and financial assistance.

Lastly but not the least, special thanks go to Mrs Mwaba from the Department of Water Affairs for typing the manual.

May God bless

F.C.P. Ndhlovu

P-WASHE Chairperson

# INTRODUCTION

The Northern Province, Provincial Water, Sanitation and Hygiene Education (P-WASHE) committee has developed a number of operation and maintenance manuals to be used in the Rural Water Supply and Sanitation (RWSS) programme.

This manual is on the borehole technology. In Zambia, and in Northern Province in particular, groundwater forms a significant proportion of water supply to the rural communities. Boreholes are becoming a common means of abstracting this groundwater to provide sufficient quantities of clean potable water for the rural communities especially during periods of drought.

## OBJECTIVE AND CONTENT

This manual is meant to serve as a guide for executing activities for boreholes. It addresses aspects associated with construction, operation and maintenance of a borehole facility in the 3-tier O&M system for Northern Province.

It presents descriptions of the technology, siting information, construction procedures, operation and maintenance requirements as well as roles and responsibilities of different players in operation and maintenance activities.

## TARGET

The manual is to be used by all WASHE committees in Northern Province.  It is however, intended to guide communities and facilitators such as V-WASHEs, pump minders, technical supervisors and Sub District-WASHEs on carrying out operation and maintenance activities.

The three players, D-WASHE, Sub D-WASHE and the V-WASHE will find it handy in performing their roles and responsibilities associated with the borehole technology.

## APPLICATION

The desired improvements in operation and maintenance will largely depend on proper utilisation of the manual.  It is, therefore, recommended that the manual be used at all levels of operation and maintenance activities.

Before construction activities, preferably during community mobilisation, sensitisation and monitoring, the requirements in the manual should be thoroughly discussed with all stakeholders.  During construction, it is inevitable that the manual be referred to step by step and all requirements stipulated therein adhered to.  It is the conviction of the developers of this manual that a properly constructed and equipped borehole will present minimal operation and maintenance problems.  Thus, in this manual, construction procedures and adherence to technical specifications have been considered as important pre-requirements for successful subsequent O&M activities.

# DESCRIPTION OF BOREHOLE

Depth

Diameter

Casing pipe, screws and bottom plugs

Gravel packing

Grouting

Centralism provision

Bottom plug and top cap

Boreholes are machine-bored wells into the ground to penetrate the water bearing formation. Generally, the diameter ranges from 100mm to 250mm.  It is lined and protected against contamination and equipped with an appropriate water-lifting device.

## BOREHOLE STRUCTURE

The borehole structure can be described under the major components shown in the box.

### Drilling depth

The depth of boreholes may vary from area to area and depends on both geological and hydrogeological conditions.  Information available at Department of Water Affairs reveals that the potential zones for groundwater occurrence have been established to be between 40-85m.  Further, other data in areas where projects have been executed reveal that aquifers are penetrated in drilling range from 25-85m.  The average depth of boreholes in Northern Province is between 45-50m.  For cost estimation the depth of 50m is often used

### Diameters of boreholes

Two borehole diameters are used in rural areas of Zambia.  These are 4” and 6’’ (100 mm and 150 mm).  This is according to the planned population to be served based on lifting devices.  The latter is selected for sites where hydrogeological conditions are favourable and population to be served likely to increase so that hand pumps are replaced by motorised systems.  In Northern Province, this is the size that has been recommended.

Steel

PVC

Fibre Reinforced Plastic (FRP)

Casing pipes and well screens:

Casing pipes are made in standard lengths of 3, 4 and 6 metres. The materials shown in the box are used for making casing pipes and screens.

In recent years, the last two have been widely used.  They are strong enough to withstand earth pressure despite their lightweight, which allows for easy handling during transportation and field works.  They also fit well for groundwater with abrasive nature because of their resistance to corrosion.  Steel casing pipes are still in use in many parts of the country especially where groundwater is not abrasive.

### Gravel packing

This is an important part of borehole installation and should be carefully done.  Ideally well-washed and graded gravel should be used as gravel packing material.  The grading is such that large particles are placed against the well screen and in diminishing size, the smaller particles placed on the wall of the borehole.

Best gravel packing material could be found in meandering riverbeds. These are usually made of quartz that withstands chemical and physical weathering. The purpose of gravel packing is

- To fill the annular space between the casing and the borehole wall.

- To stabilise the formation.

- To prevent fines from the surrounding formation falling into the borehole.

Usually the grain particle size of gravel pack is about 6mm.

### Grouting

Grouting is a process carried in borehole construction to seal off undesirable water from entering the borehole.  A strong mix of concrete is placed in sections of the borehole depth where such undesirable water can enter the borehole.

### Centralisers

Centralisers are installed in order to maintain the alignment of the casing pipes and well screens in the centre of the borehole.

## BOREHOLE DESIGN

The word “design” is used in the context of the practical realisation of a borehole meeting the demand of the population and their accepting the facility.  Among factors to consider in the design of boreholes are:

- Location:  This has been discussed under the section that deals with siting.

- It should safeguard the quantity and quality of water

- Unit supply rate of water should be targeted to meet the minimum requirement of 30 litres per capita per day and thus complying with WHO standards.

- Population to be served: Consideration should be made on the population to be served and the rate.  With the demand of 30 litres per capita per day, people to be served can be estimated from the pumping rate.

- Hygiene conditions

### Borehole structural design

The structural design of a borehole is derived from hydrogeological survey and the drilling process.  Following section 2.1.1 and considering these two processes the borehole structure is determined as follows:

- Depth usually is determined from hydrogeological survey data.

- Diameters adopted are 4 and 6” (100mm or 150mm) for rural areas.

- Installation of casing and screen:  In a typical design the plain casing is set at 80% of the total depth of the borehole while the screen takes 20% of the total depth.  Screen slots are selected on the basis of removal of fine material from the formation.  From past practice, it has been common to select a slot that retains 40% of the sediment in the formation adjacent to the screen (This applies for naturally developed borehole).  For filter packed boreholes slot sizes are selected to retain 90% of the filter pack materials.  Other issues to look at when selecting slot sizes are effects on well development, yield of the borehole and pressure drop near the borehole.

Screens are installed in water bearing sections of the borehole.  This could be in a continuous column or in staggered placement depending on aquifer positions.   A clue of screen positioning can be obtained from hydrogeological survey results and confirmed during the drilling operations.  Water bearing sections are determined by soil sampling and physical water striking where there is sufficient water in the aquifer.

Bottom plugging is important to avoid debris or fine soil material being lifted up the casing column.

## RECOMMENDED TYPE OF LIFTING DEVICE

In rural areas a borehole can be installed with windlass and bucket mechanism or a hand pump.  The bucket is a cylinder of 5-litre capacity.  There are several types of hand pumps such as India Mark II, Bush Pump and Blair pump. The recommended type of hand pump for Northern Province is India Mark II for boreholes with static water levels beyond 15m because of the ease with which it can be operated and maintained.  In Northern Province the windlass and bucket mechanism is recommended to be used only on boreholes with a static water level not greater than 15m.

## ADVANTAGES AND DISADVANTAGES OF BOREHOLES

Advantages

It is easy to use by all.

It is a hygienic way of drawing water as it is sealed.

It has less maintenance activities e.g. dewatering the pit is not necessary.

Water pressure inside can be maintained, reducing the danger of caving in.

Takes less time to construct than excavation by hand.

It is not labour intensive.

It is more reliable especially in drought prone areas.

Not easily polluted.

Deeper ground water can be accessed.

Disadvantages

It is comparatively expensive to construct and rehabilitate.

Spares are expensive and not easily available in rural areas.

Scarcity of tools and skilled manpower at local level.

Vulnerable to vandalism.

Provides low storage volume.

It is difficult to deepen an existing borehole lined with PVC casings as perturbation of the bit could result in smashed casings

Some of the advantages and disadvantages of a borehole as compared to a conventional hand dug well are listed below;

# SITING OF BOREHOLES

Siting is the selection of a most suitable point for construction of a water point.  This involves two stages, the participatory site selection and the detailed geophysics survey.

## PARTICIPATORY SITE SELECTION PROCESS

It is important that community members fully participate in the site selection process so that they accept the water facility, which in turn will lead to their willingness in maintaining it.  To ensure consensus and avoid biasness, participatory approaches should be employed in this process.

### Steps in the siting process

- Making an appointment with community

Sub district WASHE members should inform V-WASHE members about the upcoming site selection exercise.  At this stage, the V-WASHE Committee is requested to inform other Community Members about the exercise and upcoming participatory community meeting, when and where the meeting will be held.

Note: that appointments with communities should be done preferably through the V-WASHE well in advance either by sending written or radio message(s) where possible or by visitation.

- Participatory Community Meeting

Community Meetings should be facilitated by Sub District-WASHE and V-WASHE members who should:

- Give brief background to site selection by stating that their visit is a response to what the community had planned for - the borehole.  Facilitators should find out from community members how previous siting exercises were done.

- Explain the participatory process to follow in site selection exercise, how long it would likely take and technical aspects to consider during actual siting.

- Brief community members about the participatory requirements to be adhered to in the process.  Additionally, roles to be performed by community members should also be discussed.

- Request the community to provide a community map to assess social and resource features in the community.  Where a map is not available, communities should be asked to draw the community map and in the process Sub D-WASHE members should ask probing questions about the features on the map.  Keen interest should be taken in identifying where water points, latrines, animal pens or kraals, houses for the aged, the chronically ill and the handicapped, graveyards, sacred grounds are and the location of politicians and traditional leaders.

Note that community mapping will assist in preventing influential community members such as politicians from bulldozing others on where to locate the site to serve their own interests.  In addition, keep in mind features on the map to refer to and further probe communities during site visitation.

- The facilitator should divide community members into groups such as male adults, female adults, male youths and female youths and ask them their preferred sites on the community map.

- Facilitate consensus building on the order of priority after the groups present their preferred sites through ranking.

- Site visitation for actual siting

Although consensus with various groups, on the order of priority of sites would have been reached during community meeting, groups of community members tend to have competing and conflicting ideas on where the actual site should be.  Sub district-WASHE and V-WASHE members should, therefore, in the company of technical staff conduct a technical feasibility survey of all the sites chosen by community members.  At this stage, it is important to consider the following:

Local knowledge and experience:  Community’s local knowledge and experience in siting should be given high consideration.  Their experiences, for example, in divining should be discussed and if a particular person can apply divining technique, should be encouraged to do so.  Divining can be used by rural communities to detect areas where water could possibly be found by either using copper electrodes or a fresh forked twig of Musekese tree branch.

Technical aspects:  Technical aspects of importance that should be considered in siting are:

- Location

- The borehole should be sited a walking distance of less or equal to 500m from the furthest household and should not disadvantage majority of the people.

- The population size should be 20 – 40 households.

- The site should be accessible for material delivery and villagers through out the year.

- The site should be on the upper side of the slope and at least 30 metres away from latrines refuse pits, graveyards and kraals.

- Soil formations and topography

- Soil conditions must permit construction of a borehole.

- Borehole construction is best suitable in firm stable formations.  Good aquifers are either in structural discontinuities (e.g. fracturing, faults) in the rocks or from weathered horizons at the interface between overlying sediments and the rock head.

- In mountainous areas the best aquifers are found along the edges of the valley.

- Vegetation

- Presence of water loving trees such as Mukuyu tree in a particular area indicates possible availability of groundwater.

- Water Quality and Quantity

- Areas where the water table rises to less than 1 metre below the ground should be avoided, as these are prone to pollution especially in case of floods in the rain season.

- The borehole should be located at a site where there is a possibility of having clean and adequate water through out the year.

- Community Meeting to Provide Feedback

The findings of site(s) visitation(s) must be discussed with community members.  Details why a particular site could be recommended should be thoroughly discussed.  Sub district-WASHE and V-WASHE members together with the technical person should ensure that consensus is reached on the appropriate site for borehole construction. This should take into consideration participatory siting requirements to ensure social acceptance of a site by all intended beneficiaries and to be assured of community participation before, during and after construction.

Note: that the participatory process in siting will assist facilitators on planning and how to approach the intended beneficiaries.

## TECHNICAL / SCIENTIFIC SELECTION OF A SITE

Exact drilling points in the chosen sites or villages should be determined by qualified staff based on Hydrogeological and Engineering conditions. Geophysical survey is used to assess the groundwater potential of an area and further to locate an appropriate point where a borehole can be drilled.  Further more, a wide variety of methods are being used all over the world to determine the presence of water in the subsoil, including exploratory drilling, aerial surveys, seismic and geo-electrical methods.

- Geo Electrical Resistivity Measurements

With this method of siting, an electrical current from an artificial source is sent through the sub-surface.  Given the strength of the current applied, the apparent sensitivity of a part of the sub-surface can be calculated.  By varying the distance between either the current electrodes (Schlumberger Configuration) or by both electrodes (Wenner Configuration) different resistivities will be obtained.  In this respect, the further apart, the deeper the penetration of investigation.  The specialist who executes the measurements and the hydro geologist will draw curves which represent the relationship between apparent resistivity and the distance between the electrodes and will interpret the results to determine the probable structure of the sub-surface and groundwater potential.

# BOREHOLE CONSTRUCTION PROCEDURES

(NB:  A lot of the material in this section is taken from supplementary module 2B, Borehole standard construction details, DISS 2002.)

Borehole construction involves the following critical steps: drilling, casing, gravel packing and grouting, borehole development, pump testing, water quality analysis, equipping and construction of headworks.

## GENERAL INFORMATION

This section presents a framework and critical steps that precede the more detailed borehole construction processes. It outlines organisational issues and other preparatory requirements for the construction process.

### Important Considerations

It is important to take into consideration the following:

- Hygiene education incorporating gender awareness creation and HIV/AIDS sensitisation should be conducted by the sub D-WASHE and the V-WASHE committee before, during and after construction.

- All technical decisions are to be taken by the technical supervisor in consultations with the contractor’s representative or driller. The two will decide on:

- When to stop drilling in difficult formations

- The final depth of the borehole

- When to stop the borehole development process

- Any other critical technical details as stipulated in the signed contract

- It is the responsibility of the V-WASHE to ensure that the access road is prepared and the site adequately cleared for the drilling equipment and to monitor and take stock of the materials used by the contractor e.g. the type, number and size of casing pipes used.

NB: The community is the employer while the contractor is the employee.

- All necessary documents including copies of the signed contracts should be availed to the D-WASHE committee and the technical supervisor.

- The Technical Supervisor should ensure that after the borehole is completed the contractor leaves a manual of the facility installed with the community (in the custody of the Care Taker).

### Preparatory and initial works

Preparatory work is as important as the actual construction process as it sets the foundation for successful work. Information on the activities to be undertaken by the community should be comprehensive, adequate and specific. The following activities should be undertaken:

- The sub D-WASHE and the V-WASHE adequately prepares the community through a process of sensitisation, participatory health and hygiene education and mobilisation of requisite resources.

- The community clears site and prepares access road.

- The contractor meets D-WASHE committee and prepare schedule of work. Technical supervisor is introduced to the contractor.

- Technical supervisor introduces contractor to sub district WASHE and V-WASHE members. V-WASHE committee takes contractor to site.

### Supervision and monitoring arrangements

Effective Supervision and monitoring of the construction process is of utmost importance to ensure a successfully completed borehole. It is the ultimate responsibility of the community to ensure regular supervision and monitoring of progress. The following guidelines should be followed:

- The D-WASHE will appoint a technical supervisor(s) to supervise the contractor. It is the responsibility of the supervisor(s) to ensure that the contractor adheres to specifications and other contract provisions. In addition to the completion certificate, the technical supervisor should prepare a written report to the D-WASHE committee who should finally make a recommendation for payment to the contractor.

- At least one V-WASHE member, preferably the caretaker, must be present every working day. The contractor should take deliberate steps to transfer basic knowledge on the construction process to the caretaker.  By doing so the caretakers will be able to gain valuable knowledge necessary for proper operation and maintenance of the completed borehole.

- A Technical Supervisor will be responsible for the daily supervision of the construction process. This entails that he/she will ensure that the construction specifications are observed. He/she will keep records of progress and problems encountered.  Records will be kept in pre-designed borehole construction forms.

- The V-WASHE committee, through caretakers, will conduct daily monitoring of the construction process. The caretakers will keep records of daily activities including usage of materials and community involvement.

- D-WASHE monitoring of progress will be done in line with scheduled project monitoring visits and in accordance with the provisions of M&E system.

## BOREHOLE DRILLING

Various borehole-drilling methods are being employed in this country. They have been universally developed because of different geological conditions. Geological conditions range from hard rock such as granite and dolomite, consolidated formation such as sandstone, mudstone to unconsolidated types such as Kalahari sands and alluvial sediments.

In many cases, the usual drilling procedures may be varied depending on the type of formation being penetrated. For instance, two different drilling methods can be employed in completing one borehole. In an instance where hard basement is overlain by loose formation two different drilling methods may be employed. It is therefore, obvious that no single drilling method is best for all geological conditions. The drilling engineer would need to be guided by the hydro-geologist in preparing correct tools to suit the drilling procedure for a particular drilling condition through hydro-geological reports.

Borehole construction comprises the following operations.

- Drilling

- Installing the casing and screens

- Installing gravel pack

- Grout to provide sanitary protection

- Developing the borehole to ensure sand/silt free condition

### Drilling Methods

Borehole drilling and installation methods that have been developed have reached advanced stage. The scope of this manual does not allow going into real detail. Only basic principles are to be described and, are as discussed hereunder.

| Table 1: Drilling Methods |  |  |
| --- | --- | --- |
| ##### Drilling Method | Advantages | Disadvantages |
| Percussion drilling | - Low technology rigs, and therefore cheap mobilisation and operation - Needs small work area - Uses little water | - Can drill only to shallow depths because of temporary casing - Relatively slow drilling |
| Rotary drilling, direct circulation | - No limit to depth of drilling - Fast drilling - Needs no temporary casing | - More expensive as compared to percussion drilling - May pollute aquifer by drilling fluid |
| DTH and air-flush rotary | - No pollution of aquifer by drilling fluid - Needs no water - DTH is very fast in hard formation | - DTH not appropriate in soft unstable formation - Drilling depth below the water table is limited by hydraulic pressure |
| Reverse circulation | - Leaves no mud cake - Rapid drilling in coarse unconsolidated / consolidated aquifers at large diameters | - May use great volumes of water |
| Auguring | - Uses low technology, and therefore is cheap, where labour is cheap | - Restricted to shallow depths |

Note: Whatever method is employed, setting up of the drilling rig to ensure verticality of the hole is important.

- Cable Tool Percussion Drilling Method

This method of drilling involves the use of a drilling machine operating with a string of tools comprising a drill bit, a steel wire cable controlled from a derrick or mast. The drilling operation is accomplished by lifting and dropping regularly the string of tools in the borehole. The drill bit breaks the formation into small fragments. The weight of the string of tools provides the necessary impact to break the formation. The reciprocating up and down action of the string of tools mixes the crushed material with water to form slurry. The water to form the slurry is poured in the hole if there is no water in the formation being penetrated.

The slurry is removed at intervals by means of a bailer.  The slurry depth should not be allowed to accumulate to so much depth because this slows the fall of the tools and retards the rate of penetration. When there is an encounter of clay, sand is usually added into the hole to facilitate penetration.

The cable tool method is suitable in both consolidated and unconsolidated formation.

- Direct Rotary Drilling

The direct rotary drilling increases the drilling speed and reaches greater depth in most formations in relatively shorter periods than the cable tool percussion method.

The borehole is drilled by a rotating bit that cuts the formation. Cuttings are removed by continuous circulation of a drilling fluid as the bit rotates.

The bit is attached at the end of the drill pipe, which transmits the rotating action from the rig to the bit. The drilling fluid is pumped down through the drill pipe and out through the jets in the bit. The drill fluid then flows upwards in the annular space carrying the cuttings in suspension to the top. At the surface, the fluid is channelled into a settling pit where cuttings settle down. The clean fluid is then recycled and reticulated down the hole. The cycle is started for picking up cuttings.

- Reverse Circulation Rotary Drilling

This is done with the flow of drilling fluid reversed as compared with the system used in the conventional drilling. The drilling fluid and the cuttings load move upwards inside the drill tube and are discharged by a pump into a pit to settle.

This kind of drilling offers the cheapest way of drilling larger diameter holes in unconsolidated formations such as alluvial sand, silt, soft clay etc.

- Air Drilling Method

Air drilling can only be done in hard and consolidated formations. Two methods use air as a primary drilling fluid. These are direct rotary air and down the hole air hammer. In conventional reverse circulation method air is used to assist but not as a primary drilling fluid. In this method cuttings are lifted to the top by air, which after passing through the drill pipe cools the bit and comes upward in the annular space. The cuttings collect at the ground surface and are removed by use of a shovel or spade. A small volume of water or surfactant should be injected in the drill system to control dust and to lower the temperature of the air so that the swivel is cooled.

- Drilling in collapsible formation

To drill in collapsible formations, mud and foam injection drilling methods are used.

For mud drilling, drill rigs are provided with mud pumps in addition to high capacity compressors. The pump induces the circulation of the drilling fluid down the hole and up through the annular space and settles in the tank at ground level. At this point the cuttings, which are picked along by the drilling fluid are allowed to settle. Cuttings should be finely ground to enhance their lifting to the surface through up-hole velocity.

In clay formation, foam injection method is usually applied to separate the water from the mud to facilitate penetration. Certain additives are added to the foam to form the drilling fluids.

- Down the Hole Drilling

This is the second direct rotational method. A pneumatic drill operates at the end of the drill pipe striking the rock while the drill pipe rotates thereby cutting the rock formation. The percussion effect is similar to that of the cable-tool drilling bit. This method of drilling is widely used in hard and abrasive rock formations.

Information pertaining to air pressure, velocity and operation revolutions of the drilling tools can be obtained from the Department of Water Affairs and other institutional information resource centres in Water Resources Management.

- Inverse Drilling

This method of drilling is a top head drive, direct rotary system that involves the addition of air by an air-assist which passes through a special arrangement of string of tools (see illustration next page)

Compressed air is injected through an injection stem into air channels mounted outside the drill pipe and then into the drilling fluid as it moves up inside the drill pipe. The drilling fluid and the cuttings are assisted by the airlift inside the drill pipe. Use of this method can increase the capacity of a direct rotary rig to drill large diameter boreholes. . It is briefly discussed in this manual for the information of people with interest in water boreholes drilling. More information is available at the Department of Water Affairs.

### Drilling plant, equipment, tools etc.

Plant, equipment, tools and materials for the technology of drilling discussed above are outlined below. Specifications are not discussed because various models and makes of drilling plant and accessories have different specifications. The general outline is therefore, presented hereunder for information of persons interested in drilling equipment

Rotary table type

Top head drive type

Rotary spindle type

Percussion type

Drilling Rigs

Drilling rigs may be classified as in the box:

The rigs can further be classified by the method of mounting as follows:

- Truck mounted - these are mounted on trucks which are 4x2 or 4x4

- Stationery deck mounted-these are put on stationery drill table

- Trailer mounted • these are mounted on a trailer which can be towed by truck

- Crawler type-have traction chains that facilitate movement in rough and mud conditions

In Zambia, truck and trailer mounting systems are common.

Fig: 1: Cable tool percussion rig tools

The rig derrick and accessories

The engine as driver for the locomotion of the system mounted on a trailer or chassis

Control gear

String of tools i.e. drill bit, drill stem, drilling jars and rope socket etc.

The bailer equipped with valve at the bottom

Sand line

Sand pump

- Cable tool percussion rig tools and equipment: Trailer mounted and major components are as shown in fig 1.

- Rotary Rig

The following are major components of rotary drilling rigs

- Drilling derrick: The derrick is made of steel pipes or structural steel. The derrick provides the mast to facilitate the lifting and lowering of tools in the drilling operation.

- Drill Head: The drill head facilitates the lifting and connection of drill rods.

- Drill Rods:  This is an important part of the drilling rig. The rod is actually the part of the rig, which is moved by the rotating mechanism

- Core Barrels: These are steel pipes to take out core samples where necessary. They have got diamond chisel

- Drill Bits: Drill bits perform the actual cutting of the formation. They are usually made of diamond. Their configuration is dependent on the geological structure, rock quality, depth of borehole, water volume, etc.

- Lifting and lowering tools:  The following are lifting and lowering tools that can be provided with rotary rigs

- Water swivel - an instrument used to send fluids such as plain water, mud water, etc. from a pump into the interior of a rotating rod

- Hoisting water swivel - an instrument used to send water into the rotating drill rod during lifting and lowering

- Hoisting plug - connected to a rope socket and used when lifting and lowering the drill rods

- Hoisting rope socket - is a socket in the upper part of the hoisting plug to which a hoisting wire rope has been welded with rabbit metal. In operation, a hoisting plug is connected to the lower part. The assembly bearing in the socket allows it to rotate freely

- Rod holder - is a tool for holding the drill rods when they are being hoisted or lowered

- Snatch block - this is a pulley like instrument, which is usually set at the top of the derrick and used when a drill string consisting of drill rods, core barrel, and drill bit is lowered or lifted. In case the lifting weight is big, a crown block or travelling block is used.

- Travelling block- this is a floating pulley used with 2 or 3 lines to lift or lower the drilling tools beyond the capacity of the hoist.

- Crown block - this is installed at the top of the derrick and is mainly used for lifting and lowering drill strings

- Come along- this tool is used for manually drawing out and lowering drilling rods.

- Other tools such as iron ropes, lowering iron, etc., are provided for lifting and lowering

- Casing tools and accessories: These tools are described below:

- Casing pipe: this is a cylindrical tube made of either steel or plastic (PVC). It is used to prevent a borehole from collapsing. It is also used to cut off water and to cope with artesian water and gas blowouts where they may occur. There are two types of connections of casing pipes i.e. the flush joint type, which directly connects the pipes, and the flush coupled type, using couplings (sockets) at each joint (also used in other methods of drilling i.e. cable tool).

- Casing Swivel: a tool, which is used to connect the casing pipe and the drill rod for hoisting and lowering the pipes. It also enables casing the hole while drilling.

- Casing head: a thread protector to be fitted at the upper-end of the casing after it has been inserted

- Casing shoe: a tool to prevent the lower end of the casing from wearing-out

- Casing metal shoe: used for re-drilling collapsed stratum with a tube, diamond or metal tip embedded at the top and outside of the shoe.

- Casing metal bit: Used for surface drilling or drilling in a collapsed stratum with a casing tube. Diamond or metal tips are inserted on both inside or outside as well as top of the bit

- Casing band: A tool which holds the casing tubes during lifting and lowering operations

- Casing cutter: Used to cut off the casing pipe once caught in a hole or protruding above the surface after completion of the work.

- Fishing tools: The following is a list of fishing tools: -

  - Rod coupling cap - is a tool used to take out rods which are broken down the hole

  - Rod inside/outside tap - this tool is used for the purpose mentioned above. The tool is positively tapped inside (inside tap) or outside (outside tap) of the rod

  - Casing tap - core barrel tap. These taps are used to recover casing tubes/core barrels, which have dropped in the borehole. The tap is screwed into the tube/core barrel and then pulled up

  - Rod hand-this tool is used to hold a rod retained in the borehole when pulling up by means of jacks

  - Knocking block - this is a collar fixed at the upper end or joint of the rods and is used to receive the impact when hammering up or down

  - Drive hammer with chain - this tool is used for hammering up and receiving drill strings which are jammed in a hole. The drive hammer can also be used to strike in/up drive pipes

  - Pipe pulling back jack - this tool is used to pull up caught drill strings

- Engineering tools: The following engineering tools are used in drilling operations:

- Parmalec wrench: This is a tool used for screwing and unscrewing thin walled pipes like wire-line, core barrels without damaging tubes.

- Pipe wrench (bobo Jan.): Used .for screwing and unscrewing pipes such as drill pipes, core barrels etc

- Super tong: Used for screwing and unscrewing pipes exceeding 100mm in diameter

- Other engineering tools such as metal setting tools, levels, plumb bobs, vennier callipers are used in borehole construction operations

### Stratification sampling

This is an important process of gathering information in the drilling or construction of boreholes. It describes the geological formation of an area from surface to the maximum drilled depth. This process involves taking samples of cuttings at standardised depth (3m). The drilling Engineer or hydrogeologist analyses the samples and in comparison to standard lithology establishes the formation and aquifer characteristics.

## BOREHOLE CASING

Casing is the lining of the borehole using pipes. These pipes could be in steel or plastic (PVC or Fibre Reinforced Plastic) materials. In Northern Province, because of a generally low pH / high acidity of the ground water, PVC casings are recommended. Plastic pipes are also light and easy to handle and transport. Casings are made in standard lengthens of 3, 4 and 6 metres.

There are two types of casings namely the blank and the perforated. The portion below water level and the production zones should be cased using perforated casings whilst the portion above the water should be cased using blank casings. For the perforated ones, the size of the perforations is critical. It is, therefore, important to use machine-perforated casings as opposed to manually perforated ones.

The purpose of casing boreholes is to hold back the walls from collapsing. In hard and stable formations, therefore, the portion below the water table may only be partially cased. In soft and unstable conditions, however, temporal steel casings should be provided to hold the hole open while drilling proceeds. For the 150mm permanent casing pipes used in Northern Province, the temporal steel casings should be at least 200mm in diameter.

Centralisers are installed in order to maintain the alignment of the casing pipes and borehole screens in the centre of the borehole.

## GRAVEL PACKING AND GROUTING

All boreholes must be properly gravel packed and grouted.

Gravel Pack: This is an important part of borehole installation and should be carefully done. Ideally borehole-washed and graded gravel should be used as gravel packing materials. The grading is such that large particles are placed against the borehole screen and in diminishing size. The smaller particles placed on the wall of the borehole.

Best gravel packing material could be found in meandering riverbeds. These are usually made of quartz that withstands chemical and physical weathering.

Purpose:

- To fill the annular space between the casing and the borehole wall.

- To stabilise the formation.

- To prevent fines from the surrounding formation falling into the borehole.

Usually the grain particle size of gravel pack is about 6 mm and free of organic matter that could rot and compromise the water quality.

Grouting: is a process carried out in borehole construction to seal off undesirable water from entering the borehole. A strong mix of concrete is placed in sections of the borehole depth where such undesirable water can enter the borehole. The top three metres of the borehole must always be grouted.

## BOREHOLE DEVELOPMENT

This is the procedure designed to maximise borehole yields and has two broad objectives:

- Repair damage done to the formation by drilling operations so that the natural hydraulic properties are restored

- Alter the basic physical characteristics of the aquifer near the borehole so that water will flow freely into the borehole.

Borehole development also helps to achieve sand free water at the highest possible specific capacity. Therefore, all new boreholes should be developed. Older boreholes may also require periodic redevelopment to maintain or improve the original yield and drawdown conditions.

### Borehole Development Methods

Different borehole development procedures have been evolved to suit physical characteristics of aquifers and the type of drilling methods used. Any development procedure should be able to clean the borehole so that sand concentration in the water is below the maximum allowable limit for the set water use.

The following procedures can be employed in developing and or redeveloping boreholes:

- Over pumping

- Backwashing

- Mechanical surging

- Air developing by surging and pumping

- Over-pumping

In this method fine materials are removed by pumping from the borehole at a higher rate than the borehole will be pumped when put into use. The use of this method has some merit in that a borehole that is pumped sand free at high rate is always pumped sand free at lower rate. This method is more effective in filter-packed boreholes and in sandstone formations, which are non-stratified.  Pumps of reasonable capacities are required especially when large quantities of water are to be pumped.

- Backwashing

This process employs reversed flow of water through screen openings. As this is done the sediment is agitated and finer fractions removed while the remaining formation particles get rearranged. Reversing the direction of flow breaks down the bridging between large particles and screen openings that results when water flows only in one direction. The process of backflow in the backwashing cycle breaks down the bridging and the inflow then moves the fine material towards the screen and into the borehole.

- Mechanical Surging

In this method of development water is forced to flow into and out of the screen by operating a plunger up and down the casing similar to a piston in a cylinder. The tool normally used is called a surge block, surge plunger or swab. Before starting to surge, the borehole should be bailed to make sure that water would flow into it. The surge block is lowered into the borehole until it is 3 to 5 m beneath the static water level but above the screen. The water column will actively transmit the action of the block to the, screen section. The initial surging motion should be relatively gentle, allowing any material blocking in the screen to break up, go into suspension and then move into the borehole. Particular care should be taken in operating the surge block in fine sand, silt, or soft clay formations. These might slump into the screen.

As the block is lowered the force of the surging movement is increased. Development should begin above the screen and move progressively downward to prevent the tool from becoming sand locked.

- Air Developing by Surging and Pumping

This is carried out by alternately surging and pumping with air and is carried out more often in modern drilling using rotary drilling rig equipped with large air compressors. Air is injected into the borehole to lift the water to the surface. As the water reaches the top of the casing, air supply is shut off, allowing the aerated water column to fall.

Both air pressure and air volumes are important in maintaining the air surging or lifting operation. Enough pressure should be created to overcome the initial head as a result of the submergence of the airline. Air pressure of 125 PSI (862 Kpa) is capable of airlift pumping in boreholes of 90 -120m depth. Air volumes required for airlift pumping through this range of head is about 2.5 cfm. This pressure and air volume can be effectively used to carry out airlift pumping in most boreholes drilled in Zambia.

## BOREHOLE PUMPING TEST

Pumping tests are carried out soon after the drilling operations have been completed. However, pumping tests can also be performed on an existing borehole for the purpose of establishing its characteristics where information is not available. Pumping test on a borehole is carried out to determine its characteristics. Some of the important characteristics are; specific yield, dynamic water level, draw down and recovery rate. These characteristics are important as they assist in pump selection, suction head determination and to some extent pumping duration of the borehole especially for motorised systems. For the rural areas, where hand pumps would be installed, the significance of pump testing is to establish the minimum yield, which should not be less than 0.2 l/s.

### Pumping test process

The process of pump testing involves continuous pumping of water from the borehole over a certain period of time. For a percussion cable tool-reciprocating pump, the practical pumping duration has been 24 hours. For faster pumping systems such as submersible and airlifting, the pumping duration should be between 8 and 12 hrs.

The yield of the borehole is measured at a set time interval. The water level is also measured at the same time interval. This is carried out to determine the dynamic water level. Once the dynamic level is determined and set pumping duration achieved, a recovery test is carried out. As water flows into the borehole from the aquifer water level is progressively taken at a set time interval until a static condition is attained. After this operation, the most basic characteristics of a borehole are established. As mentioned above, these are: yield, dynamic water level and drawdown.

## WATER QUALITY ANALYSIS

Quality analysis is carried out alongside pump testing. This is also an important operation. Chemical analysis is carried in-situ. More complicated parameters (i.e.. Microbiological ones) are carried out at district or provincial laboratories. This operation establishes how safe the water from the borehole is according to the intended use.

## WATER LIFTING DEVICES

Indian Mark II

Indian Mark III

Bush Pump

Blair Pump

Consalen

Handpumps are recommended to be installed in boreholes for rural water supply unless usage and population demand installation of a motorised system. Many types and models of hand pumps are in use in this country. The multiplicity of hand pump models has made operation and Maintenance (O&M) rather difficult in that spare part dealers find it difficult to select which model to concentrate on to provide spare parts. In view of this situation the Government is endeavouring to standardize the type of hand pumps to be adopted for use in this country. The standardisation committee has short-listed the hand pumps shown in the box for adoption as standard pumps for use in rural water supply:

These pumps were decided upon because of the ease with which they can be operated and maintained. Since 1992/93 the Indian Mark II has taken lead in being procured and installed over boreholes. In Northern Province, this is the pump of choice.

The Indian Mark II hand pump comprises the following major parts:

- Pump head: This is an above ground mechanism fabricated in galvanised iron. It is available in different mounting arrangements.

- Connecting rods of 12 mm diameter mild steel electro-galvanised in three metre lengths with hexagonal couplings.

- Riser pipes (drop pipes) of 32 mm diameter nominal bore in three-metre length with plain socket couplings.

- Cylinder assembly consisting of cast iron body lined from inside with rimless brass liner of 63.5 mm internal diameter, gun metal valve components and nitrite rubber cup seals. It is capable of giving a discharge of 0.32 litres per second.

## RUN-OFF WATER DRAINAGE FACILITY / ABOVE GROUND WORKS

The run-off water drainage facility also known as above ground works includes the apron, drainage channel and soakaway pit.

Construction of this facility is as follows:

- Apron:

This should be as wide as possible and should be made from strong mass or reinforced concrete of 1:2:4 mix. In circular shape, it should be at least 3m diameter. If constructed in rectangular, it should have a surface area of at least 7.0 square metres. The surface configuration should slope towards the water run-off channel / drainage channel.

- Drainage Channel:

This should be as long as possible at least 4 metres. For sandy situations, however, this should be longer than 4m and preferably about 10m.  It can be made of reinforced concrete or bricks mortared together on a solid base. The gradient of the channel should be sufficient to drain off debris. However, where this accumulates, users should clear it from time to time.

- Soakaway:

Run-off water disposal normally involves a soakaway system comprising a ditch filled with stones, which can be removed for cleaning from time to time when saturated with debris.

The disposal system could also be in form of a sump constructed in the middle of a vegetable garden to provide water for irrigation. Alternatively, plants like bananas or sugarcane could be planted in an ordinary disposal area to use the run-off water. However, the new requirement is to use an improved design of a soakaway system.

- Facility Protection.

In order to restrict movement of animals around the borehole and prevent damage that can be caused to the facility, fencing off the area in which the facility is situated has been adopted in this country. A fence should be constructed of durable material such as hard wood poles, bamboo's or even brick wall. In some instances, fences are made of trees that could germinate and make an almost repair free situation. However, experts should be consulted in selecting the kind of trees to be planted to avoid trees that might deplete the groundwater through high evapotranspiration rates.

# OPERATION AND MAINTENANCE

Operation and maintenance of small community water supply systems has been neglected in the past in a great number of communities in Northern Province.  This neglect has resulted in poor accessibility, unreliability and unavailability of safe and clean water thus affecting the well being of concerned populations.  In order to reverse this, operation and maintenance should be properly implemented for the continued valuable investment in the development of water facilities in general and boreholes in particular.

## PREPARATION FOR OPERATION AND MAINTENANCE

Fig 2: Typical Caretaker selection Criteria

Self-motivated

Authority and respect to control use of facilities.

Able to carry out maintenance and small repairs after training.

Good communication with women and men about water use and hygiene.

Living near the water facility.

Seldom absent for long periods.

Likely to remain in the community.

Able to keep records.

Communities should adequately prepare for operation and maintenance. In preparation, the following should be done

- Selection of Caretakers

After siting of the borehole, the Sub District and V-WASHE should facilitate the selection of caretakers.  The Sub D-WASHE and V-WASHE should provide the community and water committee with information on issues such as HIV/AIDS, health/hygiene education, gender and environmental protection.  Selection should be done democratically taking into account selection criteria given in the box

- Training of Caretaker during Construction

During construction of the facility, the Sub D-WASHE members should ensure that the caretaker participates and gains hands-on experience on the construction.

- Community discussion on the Management of the Borehole

It is important that the community discusses all aspects relating to the management of the borehole.  This should be facilitated by the Sub-WASHE and V-WASHE using participatory approaches.

The following issues should be discussed and agreed upon:

- Rules and guidelines on the use of the borehole

The community should agree on the rules and guidelines to govern the use of the facility such as operation hours and security of the facility, restriction of certain activities in the use of the borehole and its surrounding and on hygienic practices.

- Maintenance of the borehole and its surrounding

The community should agree on who will maintain the facility and its surrounding.  This should include agreements on sharing responsibilities among men and women, tariff setting and modalities of paying fees.  It is necessary that before discussion, the O & M requirements including financial costs are well explained to the community.

- Logistical Requirements

The community should make logistical arrangements for the following:

Fig 3 (a): Initial O&M Tools

1 Spades

1 Shovels

1 Pick axe

1 x 5kg Hammer

1 x 2Kg Hammer

1 chisel (9”)

1 wooden plastering trowel

1 steel trowel

1 building trowel

1 pointing trowel

1 pliers

- Tools:

Tools in figure 3a should be stocked by the Sub D-WASHE to be accessed by communities. A minimum of two sets should be kept.

The Sub District WASHE will make arrangements for recording and storage of these tools.	Tool Kit for the installation, reconditioning and maintenance of the hand pump will also be kept at Sub District level or zone consisting of 10 handpump facilities (figure 3b)

b.  Special ToolsSelf locking clamp1 NoTank pipe lifter1 NoCoupling spanner1 NoHandle axle punch1 NoConnecting rod lifter1 NoCrank spanner2 NosLifting spanner3 NosConnecting rod vice1 NoChain coupler supporting tool1 NoBearing pressing tool1 NoTool box1 No

Fig 3 (b):

Tool Kit for installation, Reconditioning and maintenance of India Mark II Deep well Hand pumps.

a. Standard Tools

Pipe Wrench 24”

Adjustable Spanner 12”

Open ended Spanner 17mm x 19mm

Hacksaw with Spare Blade 10”-12”

Flat file 10” fine

Half round file 10” fine

Stock and die to cut 1¼ BSP threads with spare die.

Stock and die to cut M12 x 1.75 threads with spare die

M 12 x 1.75 tap set with handle

Small screw driver

Large screw driver

Engineering’s hammer ½ kg

Spirit level

Wire bush & Sandpaper

Chisel

5 metres measuring Tape

Oil can

Grease gun

Bench Vice

- Spare Parts

Spares for pump – HeadQuantityHexagonal bolts M12 x 1.75 x 40 mm long8 NosHexagonal bolts M 12 x 1.75 mm18 NosHigh tensile bolt M 10 x 1.5 x 40 mm long1 NoNyloc Nut M 10 x 1.5 mm2 NosHandle axle (stainless steel)1 NoWasher (4 mm thick) for handle axle1 NoBearing (No. 620422)2 NosSpacer1 No.Chain with Coupling1 No.Bolt for front cover M 12 x 1.75 x 20 mm long1 No

Spares for CylinderQuantityLeather sealing Cup washer4 NosLeather Sealing rings6 Nos.Rubber seating (small)2 NosRubber seating (big)2 Nos

Spares for G. I. Riser PipeQuantityHexagonal Coupling M 12 x 1.75 x 504 NosPipe sockets for 32 mm N.B. medium Grade G. I Pipes4 Nos

Table 2: Spare parts for Hand Pump, cylinder and GI riser pipes

The V-WASHE should ensure that the water committee raises funds for spare parts and that it sources for spares.  The recommended spares for India Mark II deep well hand-pump are listed below.

- Materials

In addition to the tools and spare parts, materials such as grease, stationery, manuals and wire for fencing should be bought and stocked by the community.

N.B:	For logistical requirement for a borehole fitted with windlass and bucket, please refer to the manual on wells.

Fig 4: Areas of training for Care Takers

Preventive and corrective maintenance

Health and hygiene education

Development of community borehole maintenance schedules

Fund raising and managing of finances

Cross cutting issues such as HIV/AIDS, gender and environmental protection.

Leadership on the day-to-day activities

- Training of the Caretakers in the Management of borehole

The Caretaker should be trained in technical and organisational management aspects of the operation and maintenance such as those given in fig 4:

- Description of O&M requirements

Unskilled

Users can carry out daily activities

Water committee to organise maintenance and collect, record and dispense funds for spares and repairs.

Semi-skilled

Caretaker can carry out the weekly checks and carry out preventive maintenance to the pump head

Skilled

Private sector (Area Mechanic) for concrete work

Water agency maintenance team to carry out work requiring the removal of the rising main.

Private sector/contractor to clean the borehole when necessary.

Labour

Fig 5: O&M Requirements

Available within the community

Sand for mixing cement mortar/concrete

Fencing materials

Brush for cleaning platform and drain

Record book and pen

Crashed stones

Manuals e.t.c.

Available within the province/District

Cement for platform repairs

Spare parts for pump repairs

Tools for preventive maintenance and repairs

Pipes for the rising main e.t.c.

Materials and equipment

Community funds

Labour and materials for platform repair

Purchase of hand pump spare parts

Government Funds

Back up support and major repairs

Finance

## IMPLEMENTATION OF O&M

### Organisation for implementation of O&M

Implementation of O&M activities requires well-defined structures, roles and responsibilities, a clear mechanism for decision-making and an effective support system.  With respect to boreholes, O&M will be organised as detailed in the sections below:

- Structures / roles and responsibilities

In the 3 –tier system adopted for Northern Province, O&M programmes and activities are organised at three-linked levels.  At community level there will be caretakers and V-WASHE committee whilst at sub district and district levels there will be the sub D- WASHE and D-WASHE committees respectively.

Fig 6: Composition of V-WASHE committee

Chairperson

Vice chairperson

Secretary

Vice secretary

Treasurer

Three committee members

Two borehole caretakers

The organisation of the structures and their main roles and responsibilities are as follows:

- Caretakers: the V-WASHE will facilitate the appointment / election of two caretakers by the community at each borehole. One caretaker should be female whilst the other one should be male. The two caretakers should divide their roles and responsibilities in consultation with the V-WASHE committee. The two caretakers should be members of the V-WASHE committee.

- V-WASHE committee: this committee will have overall responsibilities for all WASHE activities in a particular community including those for O&M. It will be composed of members shown in fig 2. At least 5 of the committee members should be women.

- Sub D-WASHE committee: this is an Intersectoral committee composed of extension officers, NGOs and community leaders at catchment level. The committee will have the responsibility of facilitating the engagement of Area Mechanic where necessary and bear the responsibility of reporting on all O&M activities in their catchment areas. The reporting will be done according to WASHE M&E guidelines. The committee may facilitate the selection and training of more than one Area Mechanic who could later be engaged for particular sections of the catchment area.

- D-WASHE: the committee will have overall responsibility for all district O&M programmes. In particular, the committee will facilitate the development of reporting forms and other mechanisms for documenting O&M activities at all levels. The D-WASHE will establish a central stores at the local authority for operation and maintenance of boreholes in the district.

Each of the levels above is organised according to the specific activities performed by the different players at that level. The table below gives details on specific activities undertaken by players as they perform their roles and responsibilities at a given level.

# Table 3: Roles and responsibilities of WASHE structures at different levels

| # Village level |  |  |  |
| --- | --- | --- | --- |
| ### Actor |  | Roles / Responsibility | What is done |
| ### Community |  | Conduct preventive maintenance | - Cleaning of surrounding - Observe and enforce hygiene rules - Remunerate caretaker / area Mechanic - Take care of maintenance tools |
|  |  | Raise resources for O&M | - Participate in fundraising activities - Make resource contribution for O&M |
|  |  | Disseminate health and hygiene messages | - Correct erring members of the community - Teach on how to use the borehole |
|  |  | Monitor usage of resources | - Find out progress on usage of resources from the leaders |
|  |  | Reporting | - Make verbal or written reports to caretaker |
|  |  | Manage the usage of the borehole | - Observe and enforce agreed guidelines on usage of the borehole |
| ### Caretakers | Conducting preventive maintenance |  | - Greasing of chain - Locking and opening of the borehole as scheduled - Enforce hygiene rules |
|  | Conducting repairs |  | - Mending minor cracks in apron - Unblocking of soak away |
|  | Organising community members for preventive maintenance |  | - Development of duty rosters - Preparation of maintenance schedules - Conduct meetings |
|  | Managing usage of the borehole |  | - Enforce agreed guidelines on water uses - Organise community meetings health and hygiene meetings with PHHE working groups - Put in place security measures for the borehole |
|  | Reporting |  | - Reporting faults that require attention of sub district WASHE committee - Writing maintenance reports - Writing reports on day to day running of the borehole |
| ### V-WASHE committee | Making decisions on the overall management of the borehole |  | - Conduct meetings with caretakers and community on management of the Borehole - Conduct regular V-WASHE meetings on management of boreholes - Requesting support from the Sub district WASHE for major repairs - Organising for planning activities |
|  | Conducting routine inspection of the borehole |  | - Visit water points - Conduct onsite meetings with caretakers |
|  | Organising community participation |  | - Organise fundraising activities - Mobilise community labour - Mobilise contribution of local materials |
|  | Facilitate the education of communities |  | - Link with sub district WASHE committee on PHHE and awareness creation on HIV/AIDS, gender etc - Participate in the development and usage of participatory tools especially those related to O&M |

| - Sub District Level |  |  |
| --- | --- | --- |
| ### Actor | Roles / Responsibility | What is done |
| - Area Mechanics (private sector) | Conduct major repairs which are beyond the scope of the caretaker | - Prepare tools and materials / spare parts - Repair defects together with community |
|  | Conduct training for the caretakers | - Prepare training materials - Deliver training modules in training exercises |
|  | Report to sub district WASHE committee | - Fill in pre-designed report forms - Submit forms to sub district WASHE |
|  | Provide advise (when necessary) to caretakers on how to maintain the borehole | - Conduct meetings with caretakers and V-WASHE - Write progress reports to sub district WASHE |
| - Sub district WASHE | Conduct monitoring of O&M activities | - Compile records on O&M activities by V-WASHEs - Report to D-WASHE and give feed back to community (V-WASHE) according to standard M&E guidelines. - Organise for water quality testing and monitoring on a regular basis and as required. |
|  | Training Caretakers in hardware & software components. | - Prepare training materials - Deliver training modules in training exercises - Engage area Mechanic to conduct trainings on hardware components |
|  | Facilitate selection of Area Mechanic. | - Hold community meetings to elect Area Mechanic |
|  | Conduct participatory education for V-WASHE on all aspects of O & M. | - Prepare training materials - Deliver training modules in training exercises |
|  | Planning for O & M | - Conduct regular planning meetings with V-WASHEs |

| - District Level |  |  |
| --- | --- | --- |
| ### Actor | Roles / Responsibility | What is done |
| D-WASHE committee | Constituting an O&M committee | - Conduct meeting to elect O&M committee - Develop Terms of Reference for the committee |
|  | Establish stores for spares and other maintenance materials | - Establish link with private sector - Find space for stores and establish stores system - Equip the stores with relevant tools, materials, equipment - Train stores personnel in stores management - Fix cost of spares and repairs of borehole components |
|  | Establish funding arrangements for O&M in the district | - Hold participatory meetings to determine funding arrangement - Define subsidy levels |
|  | Help the communities undertake major repairs (beyond the capacity of Area Mechanic) | - Mobilise resources for maintenance - Hold planning meetings with sub WASHEs - Provide technical advise and expertise |
|  | Monitor progress on O&M | - Develop monitoring schedules - Implement M&E system with regard to O&M |
|  | Organise district-wide needs assessment for O&M | - Implement M&E system with regard to O&M - Conduct needs assessment studies |
|  | Develop District Capacity Building plan for O&M | - Conduct capacity gap analysis - Revise capacity building plan to include O&M strategies |
|  | Documentation of O&M activities, practices, lessons and experiences. | - Conduct documentation studies |
|  | Facilitate development of mechanisms e.g. financial management and income generating, Keeping of records and usage,procurement | - Implement capacity building plan |
|  | Assist communities access vital information on O& M, suppliers, supporting agencies etc. | - Hold meetings with V-WASHE and sub district committees - Provide catalogue of suppliers |
|  | Monitor progress in O&M | - Develop monitoring schedule - Implement M&E strategies |

- Reporting Faults:

Any faults related to the functioning of the borehole noticed by the users will be reported to the caretaker who will take corrective action. Reports from users will largely be verbal but the caretaker will record all these reports in a pre-designed form for receiving such complaints.

Faults beyond the capacity of the caretaker will be reported to the V-WASHE who will in turn report to the sub district WASHE who will facilitate the engagement of an Area Mechanic. Where the V-WASHE is in direct contact with the area mechanic arrangements will be made directly with him/her.

When the Area Mechanic cannot handle a problem, the sub D-WASHE committee will make a written report to the D-WASHE committee. The report will be made on a pre-designed form stating the nature of the problem, when it occurred, any works

Fig 7:

Reporting system

for faults

done thus far and all such relevant information. The D-WASHE will make arrangements to redress the problems. The D-WASHE committee will lobby for external assistance for all problems beyond its capacity.

- Back up System:

O&M can only function sustainably where there is a working partnership particularly between the community and the government. For the purpose of maintaining boreholes in Northern Province the following should be done

- Stores: Each district will establish a central stores within the Local Authority for storage of all tools, equipment, materials and spare parts for construction and maintenance of boreholes. All local authorities will provide personnel to manage the stores. The personnel will be trained in all areas of stores management including procurement, record keeping, stock level management and entrepreneurial skills.

- Backup spares and tools: spares, tools and materials will be bought in bulk from private sector organisations with clear contractual arrangements with the P-WASHE and D-WASHE committees. P-WASHE will buy materials, tools, spares and equipment in bulk whereby doing so would reduce on costs. The P-WASHE will prepare a list of all materials that will be procured centrally.  (Refer to figure 1)

A revolving fund will be established in each district with an initial seed fund for the establishment of adequately stocked and fully functional stores. The initial seed money will come from P-WASHE. This revolving fund will be replenished periodically (3 years) from government resources and other external sources to continue subsidising O&M needs at community level. The management of funds will be done in accordance with WASHE financial guidelines and will be subject to regular internal audit and periodic external audits.

The V-WASHE and Sub district WASHE committees will have an option of buying spare parts from the D-WASHE stores at subsidised price which will be less or equal to the factory price for any given item.

- Capacity Building Plan: P-WASHE and D-WASHE capacity building plans will contain adequate provisions for development of skills at various levels for O&M. These skills will include PHHE, organisational skills, construction skills, participatory skills and financial management skills.

- Partnership with private sector: The P-WASHE and D-WASHEs will partner with reputable private sector organisations such as TAZARA workshop in Mpika for the bulk fabrication of spare parts when necessary.

Fig 8:

Some rules and guidelines

on use of borehole

No handling before washing hands

No allowing under age children to draw water

No allowing children to play at the borehole

Put a fence around the borehole to prevent animals getting access to the borehole

Lock borehole when not in use

Keep the surrounding of the platform clean and dry

Use the hand pump gently

Operate the handle with long continuous strokes without touching the top and bottom of the bracket

Operate the handle by holding it at the end

Inform the village mechanic immediately when the pump breaks down

Any washing should be done at least 5 meters away from the hand pump

Use wastewater for plantation/gardening

Clean the platform and drain regularly

Partnerships will also be developed with local contractors (registered with the Ministry of Local Government and Housing) for the construction of boreholes. A certification system will be put in place by the P-WASHE for all local contractors. P-WASHE will facilitate the training of all registered contractors in borehole construction according to the provisions of this manual. Contractors will renew their construction licences annually upon satisfaction of examination requirements before they can be considered for further contracts under WASHE.

### Day to day running of the borehole

The borehole needs to be run properly to give the intended benefits to the community. Day to day running of the borehole facility involves paying attention to the borehole so that breakdowns are minimised. In order to achieve this the following guidelines should be adhered to:

- When all preparations have been made after construction of the borehole the caretakers will draw up preventive maintenance schedules. These will include

- Scheduling of when the water point will be opened and closed

- Preparation of duty rosters for general cleaning

- Programming of community based health and hygiene education related to the use of the borehole

- Setting up mechanisms for the enforcement of rules on the use of the borehole

- All community members will wash their hands with soap or any local alternative such as ash before handling the water lifting mechanisms for the borehole. For this purpose all boreholes will be designed and constructed with a provision for hand washing.

- Transportation of water from the borehole to the point of final use is as important as the drawing of water itself.   Users will use containers with closable lids to transport drinking water from the borehole. Where open containers are used, care should be taken to ensure that fingers are not dipped into the water during transportation. Users should take necessary measures to ensure that all other sources of contamination are avoided.

- The V-WASHE committee will conduct scheduled inspection visits – preferably once in a quarter – for each borehole under its jurisdiction. During these visits the committee will hold onsite discussions with the caretakers on major problems encountered during the period and will strive to find collective solutions.

- The caretaker, using pre-designed forms, will record all issues and activities related to the day-to-day running of the borehole. Records will include registers on participation of households in general cleaning, materials used, etc.

- All materials and tools (such as keys and locks) that are relevant on a day-to-day use of the borehole will preferably be kept by the caretakers or any other community member assigned by the caretakers.

- The caretaker and the borehole committee will institute security measures where there is a likelihood that criminal activities may occur with regard to the borehole. These measures may include locking the borehole and in extreme cases making arrangements for guarding the borehole – all these will depend on the nature of the threat and what the community, collectively or through their leaders, determines as the appropriate response.

### Maintenance of borehole facility

Maintenance refers to measures and activities required to ensure the facility remains in good working condition and to limit the amount of down time to minimal levels. Practically these measures and activities are grouped into two categories namely preventive maintenance and corrective maintenance.

- Preventive Maintenance:

- Preparations for preventive maintenance will be as outlined in the section on day-to-day running of the borehole

- Preventive maintenance will be spearheaded by the caretakers and will involve regular servicing of the borehole facility to preserve and minimise its breakdown. Preventive maintenance activities will include those in the table below:

## Table 4: Preventive Maintenance Activities

| Period | Activity |
| --- | --- |
| Daily | Cleaning of surrounding and apron |
|  | Carry out an early morning test to check if the foot valve holds water in the rising main overnight |
|  | Check whether the pump delivery is normal or low. |
|  | Check if the handpump is firmly fixed in place. |
|  | Check for loose nuts and bolts on the handpump. |
|  | Clean the platform and drain. |
|  | Check the fence is in sound condition and the gate will close. |
| Weekly | Carry out daily checks |
|  | Tighten all the above ground nuts and bolts with a spanner. |
|  | Clean the accessible moving parts. |
| Monthly | Conducting PHHE to enhance hygienic practices |
|  | Carry out the weekly checks. |
|  | Collect* and record contributions to the water committee |
|  | Grease the chain |
| Yearly | Dismantle the pump head parts. |
|  | Remove the connecting rods, piston assembly and foot valve. |
|  | Inspect all the parts. |
|  | Replace worn or defective parts. |
|  | Replace piston seals. |
|  | Straighten bent connecting rods, or replace. |
|  | Replace rods with badly corroded threads. |
|  | Replace corroded or missing connecting rod lock nuts. |
|  | If connecting rods show severe corrosion, remove the rising main. |
|  | Check the rising main and replace badly corroded pipes - check the threads in particular. |
|  | Clean pipe threads and install the rising main. |
|  | Re-assemble and replace the below-ground parts. |
|  | Assemble the pump head. |
|  | Check the pump operation and pump until the water delivered is clean. |
|  | Record all significant actions. |
| Irregular | Landscape the area around the borehole |
|  | Prevent soil erosion around the apron by laying bricks around perimeter of the apron and drain and ensure that the bricks remain in place. |
|  | Prevent the construction of sources of contamination within distance of 30 m from the borehole |
|  | Organise fundraising activities for the maintenance of the borehole |
|  | Repair cracks with cement mortar in the pump platform and drain. |
|  | If pump mounting bolts become loose in the concrete platform, remove pump, breakout old bolts, and remount in fresh concrete. |
|  | Arrange to clean the borehole if the pump delivers cloudy water with silt. |
| * The time interval for the collection of payments will depend on local circumstances such as the seasonal income pattern. |  |

Source: IRC (1995): Making your Water Supply work  - Operation and Maintenance of small Water supply systems

- Environmental protection

The state of the environment can directly affect the quality and yield of the borehole.  Maintenance of the borehole in this case will include basic water resources management activities besides the protection of the environment around the borehole.

- The community will protect catchment areas for ground water, which directly and indirectly contribute to the yield in the borehole.  This will involve prevention of deforestation and instituting aforestation where necessary. It will also include following procedures on proper positioning of latrines. The community through the V-WASHE will ensure agricultural chemicals (fertilizers, pesticides and herbicides) do not result in the pollution of the water borehole. Preferably all agricultural activities involving the use of fertilisers will be positioned at a minimum distance of 100m.

- Participatory activities on how men and women use the borehole catchment area and the borehole itself will be conducted by the V-WASHE and the sub district WASHE to raise awareness on how some of their activities in the catchment may contaminate the borehole.

OBSERVE!!!!!

Deforestation and burning of grasslands

Removes the absorptive capacity of land to retain and slow the drainage of water.  The resulting rapid run off and reduced ground water recharge can result in water drying up.

- The V-WASHE and the community will monitor and document all activities happening in their area that are likely to affect the borehole.

- The caretaker and the V-WASHE will manage water use for the borehole to avoid over exploitation of the water resource, which may lead to adverse effects such as drying up of the borehole. The V-WASHE should note that over exploitation of ground water sources by both manual and motorised pumping for agricultural purpose could result in declining ground water levels.  If measures are not taken to limit water abstraction, the effect on domestic boreholes may be disastrous.

- Corrective maintenance:

Corrective maintenance involves the restoration of a borehole to its normal operating condition after a breakdown. This involves minor and major repairs. These repairs must be done with minimal down time of the borehole and minimal inconvenience to the users.

Fig 9: Minor Repairs

Mending cracks on the apron and drains

Unblocking the soak away when it blocks

Tightening loose nuts and bolts on the handpump

Repairing fence

- Minor repairs

This refers to all repairs that will be done by the users with tools and materials available in the community.  Fig 9 gives some of the activities that will be done on minor repairs.

- The caretakers and the V-WASHE will be responsible for organising for these repairs. Reporting of faults will be done as outlined in the section on “reporting faults - under organisation”.

The V-WASHE will monitor the progress of the minor repairs and keep all records and case histories of all repairs in standard pre-designed forms that will state the date and nature of the problem, nature of the repair, materials used and by

Fig 10: Major Repairs

Deepening of borehole

Fishing out of pump components eg cylinder

Redevelopment of the boreholes (cleanout)

Replacing the apron and drain

Overhauling of the handpump

Replacement of below surface components of the handpump

who, site details, etc.

- Major repairs

This refers to the correction of major defects by local and external people to enable the borehole to function as originally intended. Major repairs will include those in fig 10

- The V-WASHE and the sub district WASHE committees in conjunction with the D-WASHE committee (when necessary) will be responsible for organising these repairs. Reporting of faults will be done as outlined in the section on “reporting faults’’ - under organisation.

- The V-WASHE will monitor the progress of the major repairs and keep all records and case histories of all repairs in standard pre-designed forms that will state the date and nature of the problem, nature of the repair, materials used and by who, site details, etc.

NB: For pump installation and detailed operation and maintenance activities refer to the India Mark II Deep Well Handpump Installation and Maintenance Manual.

### Resource mobilization for O&M

Operation and maintenance require human, material and financial resources.  These need to be mobilised and be made available if implementation of O&M is to be effective.  While human and material resources have been available in many O&M systems, a lack of or inadequate financial resources has been the cause of O&M system failure.  In the three-tier system, adopted for Northern Province, a greater responsibility for O&M has been placed on the user.  The community is, therefore, responsible for raising money required for O&M activities.  External support agencies or government will only supplement community efforts by providing funds for major works such as the rehabilitation of the borehole.  The community is, therefore, under an obligation to develop mechanisms for raising and managing funds.  The following sections should help communities on developing mechanisms for financing O&M activities:

- Estimation of recurrent costs

Sub-district WASHE must assist the community in estimating operation and maintenance costs.  They should proceed as follows:

- Identify and quantify materials (grease, cement, etc) and spare parts e.g. leather cup washers, foot valves, rubber seatings, which would be required in a particular year (include other indirect O&M costs such as transport and the remuneration of caretakers and Area Mechanic where applicable).

- Cost these

- Divide the cost in (ii) by the number of households (taking cognisance of the incapacitated or vulnerable) to obtain the expected contribution from each household per year.

- The community should then agree on household contribution (set tariff) based on the results in (iii) above.  i.e. the O&M tariff can be calculated as shown in the formula below:

Indirect + direct O&M cost

Eligible number of households

O&M Tariff  =

NB: 	Some members of the community may choose to contribute in kind (agricultural produce) and must not be discouraged.  Agricultural produce contributed by the community should be sold as quickly as possible to avoid losses through rodents and pests.

- Sourcing for funds

Communities will source for funds for O&M from their own contributions.  They can also source for funds, especially for major repairs from external financing agencies or government.  Communities will access external funding by preparing a project proposal and forwarding a request to D-WASHE through Sub-District WASHE.

The following are other community initiatives that are used and should be explored and suggested to other communities:

- Community fund raising projects such as:

  - Brick moulding and selling of burnt bricks

  - Community farming

  - Working in other people’s farms at a fee (ichima)

  - Community Credit Schemes – subject to obtaining money lenders licence from the Local Authority.

  - Beer brewing, e.g. Katata (avoid illicit brew such as Kachasu)

- Drama groups.  Innovative communities can raise funds from drama performances while at the same time providing entertainment for community members especially children.

NB:	Penalties should be instituted for community members deliberately not paying the fees.  Communities will decide on appropriate penalties for defaulters.

- Management of funds

All funds raised for O&M should be used to finance O&M activities.  They should be accounted for as provided in the financial guidelines and utilised in accordance with community resolutions.  The community is the ultimate authority in deciding on how their funds should be spent.

The Treasurer will prepare financial reports on income and expenditure at a frequency agreed upon by the community, normally quarterly.

- Required Financial Skills

Basic financial management skills are required in order to effectively generate, manage and utilise O&M finances. These include basic skills in simple book keeping, record management, entrepreneurship and community organisation.

## TROUBLE SHOOTING

The table below gives some common problems with boreholes and actions to be taken

## Table 5: Trouble Shooting

| Trouble | Causes | Remedy |
| --- | --- | --- |
| - Pump handle works easily but no flow of water: | - Water level gone down below the cylinder assembly | - Add more pipes and rods. |
|  | - Worn out cylinder leather cup washer. | - Overhaul the cylinder and replace the leather cup washer. |
|  | - Connecting rod joint disconnected. | - Pull out the pump and join the connecting rod wherever necessary. |
|  | - Valve seats worn out | - Replace valve seats. |
|  | - Pump cylinder cracked. | - Replace cylinder assembly. |
| - Delayed flow or small flow. | - Damaged rising main | - Replace the damaged pipe or disconnect the affected rising main. |
|  | - Leakage in cylinder check valve or upper valve. | - Overhaul cylinder. Replace rubber seats. |
|  | - Leather cup washers worn out. | - Overhaul the cylinder and replace leather cup washers. |
| - Folding of chain during return stroke | - Improper Commissioning | - Adjust the length of last connecting rod by cutting and taping suitably. |
|  | - Leather cup washers getting jammed inside the cylinder | - Overhaul the cylinder and replace leather cup washers. |
| - Noise during operation: | - Stand assembly flange not levelled properly. | - Level the flange. |
|  | - Bent connecting rod | - Change the defective rod. |
|  | - Off-set of Hexagonal coupler welded | - Change the defective rod. |
| - Shaky Handle | - Loose handle axle nuts. | - Tighten handle axle nuts. |
|  | - Worn out ball bearings. | - Replace ball bearings. |
|  | - Spacer damaged or short in length. | - Replace spacer. |
|  | - Bearings loose in the bearing housing. | - Replace the handle assembly. |

## FINAL REMARK

The purpose of a manual is to guide the user on how to perform activities relevant to a particular technology and its relevance and importance therefore lies in its being used.  This manual is the master key that users should use to open the doors for the borehole technology. It opens the door for construction to reveal the inner contents in the construction room, the door to operation and maintenance room to reveal the inner contents in that room etc.  Thus unless this manual is read through and referred to by those it is intended, it will be of little value.  Not all contents will be relevant to all the users.  Users are therefore referred to appropriate sections for specific activities or issues.

In an attempt to answer a lot of questions in one manual, the document has been made large but convenient.  Convenient in the sense that issues concerning organisation, construction and operation and maintenance have been addressed in this one manual. The manual recognises the target groups and the fact that boreholes are extremely expensive installations, which should be properly constructed and maintained for the communities to derive maximum benefit.  Thus, it has been presented in the simplest language possible and with finer details, which would have normally been excluded.  It is recommended that this manual be orderly disseminated and used.