WATER SUPPLY AND SANITATON PROGRAMME

FOR NZOIA CLUSTER

PHASE II TOWNS – Kakamega, Busia, Nambale

FEASIBILITY REPORT – NAMBALE

TABLE  OF CONTENTS

E	EXECUTIVE SUMMARY ………………………………………………………………………………..… ……. ….. ES-1

E1	INTRODUCTION………………………………………………………………………………… … …………………..ES-1

E2	PRESENT SITUATION…………………………………………………………………………………………… ……ES-1

E2.1 Existing Water Supply System……………………………………...…………………………………………..………ES-1

E2.2 Existing Sanitation System……………………………………………………..………..  .……………………...ES-1

E3	POPULATION AND WATER DEMAND………………………………………………………..…  ………………….ES-1

E4	PROPOSED REHABILITATION MEASURES AND COSTS………………………………..…   ...……………….ES-2

E5	PROPOSED EXPANSION MEASURES AND COSTS……………………………………….…………………......ES-2

E5.1 Water Supply System…………………………………………………………………………………………………....ES-2

E5.1.1 Alternative Scheme 1 – Gravity Scheme from Malakisi River…………………...........................…….…..ES-2

E5.1.2 Alternative Scheme 2 – Pumping Scheme from Sio River………………………………………….….…....ES-3

E5.1.3 Alternative Scheme 3 – Supply by Pumping from Busia Treatment Works ………………………….....…ES-3

E5.1.4 Alternative Scheme 4 – Supply from Boreholes ………………………………………..…..………………..ES-3

E5.1.5 Economic Comparison of the Alternative Water Supply Schemes …......................................................ES-3

E5.1.6 Recommended Alternative ………………………………………………………………………..……....…..ES-4

E5.2 Sanitation System …………………………………………………………………………..…………………......ES-4

E6	WATER AND SANITATION SERVICE PROVIDERS ………………………………………………………………ES-5

.E7	FINANCIAL CONDITIONS ………………………………………………………………………………………….....ES-5

1.	PRESENT CONDITIONS	1-1

1.1	Administrative and Geographical Description	1-1

1.2	Physiographic and Natural Conditions	1-1

1.3	Socio-Economic Situation	1-1

1.3.1	General	1-1

1.3.2	Methodology for Socio Economic Data collection	1-4

1.3.3	Checklist For Socio-Economic Focus Group Discussions (FGD)	1-5

1.3.4	Socio Economic Infrastructure – Nambale Township	1-6

1.3.5	Water Supply Situation	1-7

1.3.6	Sanitation Situation	1-7

1.3.7	Housing	1-8

1.3.8	Disease Patterns	1-8

1.3.9	Participatory Mapping	1-10

1.3.10	Income Levels	1-10

1.3.11	Livelihood and Gender Participation	1-11

1.3.12	Priority Ranking of Socio Economic Parameters	1-11

2.	EXISTING WATER SUPPLY SYSTEM	2-1

2.1	General	2-1

2.2	System Components	2-1

2.2.1	Source	2-1

2.2.2	Storage Tanks	2-1

2.2.3	Distribution System	2-4

3.	ENVIRONMENTAL AUDIT OF EXISTING WATER SUPPLY SYSTEM	3-1

4.	EXISTING SANITATION SYSTEM	4-1

5.	DEMOGRAPHIC TRENDS AND FUTURE WATER DEMAND	5-1

5.1	Demographic Trends	5-1

5.2	Potential for Physical Growth	5-2

5.3	Population Projections and Distribution	5-2

5.4	Population Distribution	5-4

5.5	Future Water Demand	5-5

5.5.1	Methodology	5-5

5.5.2	Supply Area	5-6

5.5.3	Water Demand	5-6

a)	Residential Water Demand	5-6

b)	Institutional Water Demand	5-7

c)	Industrial Water Demand	5-8

5.5.4	Overall Water Demand	5-8

5.5.5	Recommendations	5-9

6.	PROJECT GOALS	6-1

6.1	Development Goal	6-1

6.2	Project Objective	6-1

6.3	Target Groups and Priorities	6-3

6.3.1	Target Groups	6-3

6.3.2	Priorities	6-3

7.	WATER AND SANITATION SERVICE PROVIDERS	7-1

7.1	Appointment of Water and Sanitation Service Providers	7-1

7.2	Evaluation of Existing of Water and Sanitation Service Providers	7-1

7.3	Proposed Organization Setup – Western Water Service Company Ltd.	7-2

7.4	General Initial Assistance in Establishment of Water Service Providers (WSP)	7-4

7.4.1	Recommendations	7-4

8.	EXISTING ASSETS	8-1

9.	REHABILITATION MEASURES FOR EXISTING WATER SUPPLY SYSTEM	9-1

10.	PROPOSED EXPANSION OF THE WATER SUPPLY SYSTEM	10-1

10.1	General	10-1

10.2	Surface Water Sources	10-1

10.3	Ground Water Potential	10-1

10.4	Alternative Schemes for Expansion of Water Supply to Nambale Town	10-4

10.4.1	Alternative Scheme 1	10-4

10.4.2	Alternative Scheme 2	10-8

10.4.3	Alternative Scheme 3	10-10

10.4.4	Alternative Scheme 4	10-12

10.5	Economic Analysis of the Alternative Water Supply Schemes	10-17

10.5.1	Project Costs	10-17

10.5.2	Discounted Cash Flow Analysis	10-19

10.5.3	Conclusion	10-21

10.5.4	Recommendation	10-21

11.	PROPOSAL FOR DEVELOPMENT OF A WATER BORNE SANITATION SYSTEM IN NAMBALE TOWN	11-1

11.1	General	11-1

11.2	Sewerage Drainage Area	11-1

11.3	Estimation of Wastewater Generation	11-1

11.4	Options for Wastewater Treatment	11-4

11.5	On-Plot Sanitation and Hygiene Campaigns	11-6

11.6	Components of the Proposed Nambale Sewerage System	11-6

11.7	Cost of the Proposed Nambale Sewerage System	11-7

12.	FINANCIAL ANALYSIS	12-1

12.1	Introduction	12-1

12.2	Principles and Procedures	12-1

12.3	Project Costs	12-4

12.3.1	Investment Costs	12-4

12.3.2	Operation and Maintenance (O&M) Costs	12-6

12.3.3	Working Capital	12-9

12.4	Benefits	12-10

12.4.1	Water Charges	12-10

12.4.2	Tariff Structure	12-11

12.4.3	Revenues	12-13

12.4.4	Other revenues	12-13

12.5	Project Financing	12-14

12.6	Financial Analysis	12-17

12.6.1	Profitability Analysis	12-17

12.6.2	Cash Flow Analysis	12-18

12.7	Conclusions	12-20

List of Appendices

Appendix A: Costs Used in the Economic Analysis

Appendix B: Financial Analysis

# PRESENT CONDITIONS

## Administrative and Geographical Description

Nambale Township is located in Nambale Division, 15km southeast of Busia Town. It is one of the six administrative divisions of Busia District. The administrative authority of Nambale Township is the Nambale Town Council. Its jurisdiction covers a total area of 74km2, out of the total area of 232km2 that Nambale Division covers. The area of Nambale Division not under the jurisdiction of Nambale Town Council i.e. 158km2 is under the Busia County Council.

Figures 1.1 & 1.2 on pages 1-2 and 1-3 show the locations of Busia District and Nambale Township respectively.

## Physiographic and Natural Conditions

Busia District falls within the Lake Victoria Basin. The altitude rises undulatingly from about 1,130m above sea level in the shores of Lake Victoria on the extreme southern end to an average of 1,375m in the central and northern regions. The altitude in the Nambale area is 1220m. The prominent geographical features in Nambale area include the Walatsi and Nambale swamps. Nambale Town is located in between the two swamps.

Climate: The annual mean maximum temperature ranges between 26 degrees and 30 degrees centigrade. The annual mean minimum temperature varies between 14 degrees and 18 degrees centigrade. The mean annual rainfall is 1750mm.

Soils: The majority of the soils consist of well drained, deep brownish Sandy clays with high natural fertility.

Drainage: Drainage is though a system of perennial rivers, the most important of these being the Sio River with its major tributaries, the Walatsi and Nambale Rivers.

## Socio-Economic Situation

### General

The socio-economic analysis was carried out for Nambale Township. The main objective of the socio-economic survey was to collect and analyse the socio-economic data related to water supply and sanitation services.

The key areas of the study are six–fold as follows:

- To assess the need and demand for water and sanitation services in the towns and form a basis for resource allocation.

- To provide information on accessibility to safe water, the sources with respect to gender issues on water and sanitation and the level of community involvement.

- To provide information that is required for participatory planning of water and sanitation activities leading to better understanding of the distribution of water and sanitation facilities and close the gap between what is existing and what needs to be planned.

Figure 1.1 Location of Busia District in Kenya

Figure 1.2 Location of Nambale Township

- To examine the social-cultural factors that affect community participation in water and sanitation provision - societal, religion, hygiene customs etc.

- Assess the parameters that influence water and sanitation demand(Income and price elasticity)

- Assess the willingness to pay and affordability of water and sanitation services to target groups and especially the vulnerable segment - urban poor, women and children.

### Methodology for Socio Economic Data collection

The Team undertook a review of existing documentation, previous surveys and relevant literature, followed by Key informant interviews of the stakeholders and opinion leaders. Focus group discussions with various groups and stakeholders were done using participatory learning process based on participatory action research methodologies. Table 1.1 shows the key tools used.

Table 1.1 - Key Tools Used in Socio-Economic Analysis

| Tools/method | Objectives |
| --- | --- |
| - Participatory mapping (Social and resource maps) | Provide baseline information for water and sanitation situation in the study areas |
| - Transect | Verify participatory mapping information, analyze existing resources in the community, established rapport with community members and provide opportunity for household interviews and assessment of water and sanitation situation |
| - Disease severity ranking | Identify common disease patterns , mortality and morbidity rates |
| - Gender task/access/resource analysis | - Identify and appreciate community gender roles as pertains to water and sanitation situation - Analyze problems and roles reversals in water and sanitation - Analyze the factors that hinder equal gender participation in water and sanitation |
| - Livelihoods analysis | Analysis of existing resources in the community, how it is utilized and factors contributing to community expenditures |
| - Focus group discussion | Finding out communities perceptions on water supply and sanitation situation What can be done to improve the situation? Discuss willingness to pay and affordability of water and sanitation services? |
| - Sanitation Ladder | Assess communities sanitation level Discuss communities desired sanitation options/technologies What can be done to improve the situation? Socio-cultural factors and perceptions that hinder sanitation promotion and adaptation |
| - Wealth and well being ranking | Assessment of communities socio-economic status Poverty assessment and access to water and sanitation services |
| - Participatory mapping (Social and resource maps) | Provide baseline information for water and sanitation situation in the study areas |
| - Transect | Verify participatory mapping information, analyze existing resources in the community, established rapport with community members and provide opportunity for household interviews and assessment of water and sanitation situation |
| - Disease severity ranking | Identify common disease patterns , mortality and morbidity rates |
| - Gender task/access/resource analysis | Identify and appreciate community gender roles as pertains to water and sanitation situation Analyze problems and roles reversals in water and sanitation Analyze the factors that hinder equal gender participation in water and sanitation |
| - Livelihoods analysis | Analysis of existing resources in the community, how it is utilized and factors contributing to community expenditures |
| - Focus group discussion | Finding out communities perceptions on water supply and sanitation situation What can be done to improve the situation? Discuss willingness to pay and affordability of water and sanitation services? |
| - Sanitation Ladder | Assess communities sanitation level Discuss communities desired sanitation options/technologies What can be done to improve the situation? Socio-cultural factors and perceptions that hinder sanitation promotion and adaptation |
| - Water Ladder | Identify communities water options Socio-cultural factors associated with water use and the desired options |
| - Wealthy and well being ranking | Assessment of communities socio-economic status Poverty assessment and access to water and sanitation services |

### Checklist For Socio-Economic Focus Group Discussions (FGD)

Water Usage and Sanitation

- Satisfaction of user demands of women, men rich and poor

- Ratio of perceived cost benefits for women, men and the poor

- Access to the water service and sanitation for poor households

- Uses of water by women/men and poor households

- Households with no access to water and sanitation facilities. Why? And what alternatives in place?

- Reasons why households and communities are not using the water supply.

Water and Sanitation Beliefs

- General perceptions of community and personal illness; tolerance for diseases

- Concept of clean water and sanitation. Perceived relationship between water and health.

- Traditional beliefs concerning excreta and sanitation practices.

- Personal hygiene habits/practices

Community Economic Patterns

- Means of subsistence

- Preferred spending patterns and ability to pay

- Cooperative and credit system

- Indirect measurement of average household income based upon determination of housing type and evident amenities

### Socio Economic Infrastructure – Nambale Township

Administration

Nambale Town Council has 6 wards namely Khwirale, Kisoko, Munyalo, Lwanyange, Tangakona and Township.

Education

Township has 2 primary schools and 1 secondary school. Literacy level is considered higher compared to other parts of the District.

Transport

The Township is accessible through the Kakamega-Mumias-Busia tarmac road.

Population

Nambale Township Location has a population of about 25,615 comprising Siekunya Sublocation with 5,932, Nambale Sublocation with 12,566 and Kisoko with 7217 people.

Health Facilities

The Township is served by the Nambale health centre which is presently being proposed for upgrading to the level of sub-district hospital. The following are the most prevalent diseases in the division based on the priority ranking are; Typhoid, Diarrhoea, Dysentery and Malaria. According to the Divisional health personnel, there is an increase of diarrhoea and malaria cases during the rainy seasons. 396 diarrhoea cases were reported between February to December 2004, while between February to September 2005, 369 cases were reported. Malaria cases reported during February to December, 2004 were 654 cases, while in February to September 2005, 677 cases were reported. The cases seem to have increased this year due to high rainfall experienced.

Economic Situation

The main economic activity in the area is agriculture and the main crops grown are y sugarcane, cotton, maize, sunflower, cassava and sorghum. Other crops include bananas, peas, potatoes, simsim and vegetables.

Brick making is a major activity in the Township area and its outskirts. Women groups in the Town are securing business loans from micro-finance institutions i.e. Kenya Women Finance Trust, Dannida and Action Aid. The following are the type of business supported by microfinance institutions; Dairy farming, poultry, brick making, cotton farming and production. According to records the Township has 50 active groups of which 10 are youth groups, 30 women groups, 7 self help groups and 3 community based organizations.

The Cotton ginnery which is operating below capacity due to mismanagement and administrative problems is the main industrial institution in the Town. Action Aid is presently working with specific women groups to re-activate the industry.

### Water Supply Situation

The Nambale Water Supply Scheme was developed in 1992 by Kenya-Finland Western Water Supply Programme (KEFINCO). The water source is 2nr boreholes, one located at the Health Centre compound and the other at the ACK Church compound.

The population presently served is approximately 11,000 people. The maximum current water production capacity is 288m3/day. This is 29% of the approximate demand of 1000m3/day in the Nambale Township service area.

Due to the shortfall in water supply various alternative water sources are in use including:

    - River water – majority of the population use river water that is polluted.

    - Shallow wells

    - Water vendors who supply water to the residents of the Town for Kshs. 5-10 per 20 litre jerry can

The following are the key factors affecting the effectiveness of the water supply based on interview of the water officials

- Inadequate staff of the right cadres and shortage of staff due to the effects of a staff retrenchment program

- Poor revenue collection due to poor record keeping and few line patrols to determine the number of consumers.

- Inadequate and unreliable water supply.

- Inadequate tools and equipment for operation and maintenance.

- Poor design and workmanship of the scheme.

- Vandalism of the scheme components by frustrated consumers due to inadequate water supply to communities.

- Unreliability of the water supply due to technical problems. The 2 functional boreholes are overworked and inadequate storage capacity has contributed to a poor or ineffective distribution.

### Sanitation Situation

The sanitation situation is wanting and inadequate:

- 95% of the town’s population depend on pit latrines while 1% depend on a waterborne sanitation system (septic tanks).

- The Town has no storm water drainage system

- The Town has no refuse collection services.

The Town Council has no capacity to manage solid waste and lacks a waste collection truck. This has resulted in crude dumping of the waste by the community members in the open ground. Some communities or estates have compost pits but the majority within the Township dump their waste into the streets or backyards.

Sanitation problems in Nambale are attributable to the following factors:

- Lack of a sewerage system due to inadequate water supply

- Absence of solid waste dumping sites and a waste collection system

- Absence of a storm water drainage system

- Pollution of ground water sources due to latrines being sited close to the water wells that most community members rely on for their water supply

- The local community’s culture of not sharing latrines with in-laws has contributed a lot to defecation in open areas around the Township

### Housing

Housing in Nambale can be categorised in three classes: medium class, low class and rural. Table 1.2 shows the characteristics of these housing classes.

Table 1.2 – Characteristics of Housing Classes in Nambale Township

| Class | Location / Description | Characteristics |
| --- | --- | --- |
| Medium | Brick houses with iron sheet roofs Within the sugar belt and close to School/church | - Rent: Kshs1500-3000 - Good permanent houses - Water connected - Electricity available - Water borne sanitation system in place (Septic tanks) |
| Low | Within or neighbouring the Town | - Rent: Kshs 500-1500 - Accessible and habitable - Near essential facilities - Community using open wells drawing water with bucket and rope - Residents Use pit latrines shared between several shops and houses |
| Rural | Next to town but has a village set up | - Semi permanent houses - Grass thatched - No essential facilities - Mostly owner occupied. - No water in the homes community fetch water from unprotected spring and nearby streams - Some homes have latrines while others do not. Some residents use the open ground as toilet facilities. |

### Disease Patterns

The chart below shows disease patterns and morbidity for Nambale Township for January to July 2005, based on Nambale Health Centre records.

Common diseases identified in the community are:

| Diseases affecting children based on priority ranking | Diseases affecting adults based on priority ranking |
| --- | --- |
| - Malaria - Pneumonia - Diarrhoea - Worms - Skin Diseases | - HIV/AIDS - Malaria - Pneumonia - Diarrhoea - Eye Infections |

#### Analysis and outcomes of diseases patterns

  - Most of the diseases prioritized i.e. diarrhoea, eye infections, skin disease and intestinal worms are due to inadequate water supply, absence of sanitation facilities and lack of hygiene promotion. Currently the water supply is not able to meet the demand due to low capacity and other technical reasons. The poor sanitation situation is partly attributed to open defecation by community members due to socio-cultural beliefs.

  - The water supply area is known to have experienced an outbreak of water related diseases and epidemics i.e. Typhoid

  - From the morbidity rates, malaria is leading followed by respiratory infections and diarrhoea. Respiratory infections have been attributed to poor housing and congestion in homes.

  - Pneumonia and malaria are common among both children and adults.

  - HIV/AIDS is noted to be common among the adults but is not reflected in the morbidity rates from the district hospital records.

Hygiene and sanitation promotion is lacking in the water supply area and siting of wells close to latrines is very common especially within the Township area where all shops have water and sanitation facilities in their backyards

### Participatory Mapping

#### Outcome of the participatory mapping exercise in Manyole Village

    - Manyole village has 100 homes with approximately 300 people

    - The community has indicated that the pipeline that the water supply to the village is inefficient and inadequate due to lack of a water storage tank.

    - Most villagers have no access to adequate sanitation facilities hence the use of the bush and open defecation.

    - The water demands are high and the community would prefer communal taps where a water committee manages the tap on behalf of the community. The community requests that the school have an individual connection to serve the school population.

    - The school within the village has no access to safe water. The school population is currently using water from a hand dug well with a bucket and rope to draw water.

### Income Levels

Community well being and wealthy ranking as discussed and presented by sampled community (Manyole Village)

| Indicators | Low income “Abamanani” | Middle income “Abenyalakho” | Well-off “Abainda” |
| --- | --- | --- | --- |
| Population size | 65% of the community | 20% of the community | 15% of the community |
| Family size | 6-8 children and at least 2 wives | 5-6 children With 2 wives | 3-4 children 1 wife |
| Assets | At least 1 acre of land, Bicycle, 2 cows and several chicken | 2-3 acres of land, Bicycle or motorbike At least 1 or 2 Grade cows | 4-5 acres of land, Vehicle, Several grade cows Farm employees |
| Occupation and type of employment | Peasants, Self-employed i.e. making bricks Boda boda taxi operators | Office clerks, Teachers And small scale businessmen | Bank employees, School principles and Businessmen |
| Levels of income | Kshs. 400-2,500 per month | Kshs 7,000-10,000 per month | Over Kshs.25,000 per month |
| Access to water and sanitation services | No access to safe water. They fetch water from streams and use open defecation system | Hand dug wells and water from streams/unprotected springs Some have traditional pit latrines | Some have access to tap water, hand dug wells fitted with hand pumps, Others ferry water with vehicles from springs/streams Have ventilated improved pit latrines |
| Educational level | Primary education up to class 8 | “O” Level education | “O” Level education, University and college education |
| Nutrition status | Breakfast of porridge Lunch of sweet potatoes/ Cassava Supper of ugali with vegetables | Breakfast of Tea with groundnuts/sweet potatoes Lunch of Ugali or githeri Supper of Ugali/ with vegetables / omena | Breakfast of Tea with milk and bread Lunch of ugali with Chicken Supper of rice wth Chicken |
| Housing | Grass thatched /mud wattle | Semi-permanent (2-3 bedrooms) | Permanent house |

Analysis and Outcome of community wellbeing and wealthy ranking discussions

- Communities in the water supply area prefer communal water points to be managed by specific water committees and the community to pay the water bill jointly. The well-off members of the community require individual connections to address their increased water demands.

- Active participation by the community in construction of the scheme during the rehabilitation and augmentation has confirmed their willingness to pay for the water services. The demand for water is high due to inadequate water supply. Also the income levels are relatively higher than the other communities under study.

- Most of the low income community members are using open defecation due to inadequate hygiene and sanitation promotion. Also digging of pit latrines is difficult due to the existing hard formation and the exorbitant cost of hiring diggers. The communities are attached to socio-cultural beliefs of not sharing latrines with in-laws therefore they prefer more than one pit latrine of simple design between an improved ventilated pit latrine and the traditional latrine i.e. San-plat or ecological sanitation based on alternating pit latrines or forsae-alternae.

### Livelihood and Gender Participation

Community ranking of various businesses based on gender implications and start –up capital.

| Type of business | Who operates and controls the business? | Start-up capital |
| --- | --- | --- |
| - Brick making | Men | Kshs. 2,000 |
| - Sand harvesting | Men | Kshs. 500 |
| - Buying and selling of cereals | Women | Kshs. 1000 |
| - Retail shop/Kiosk | Men | Kshs. 5,000 |
| - Vegetable production and selling | Women | Kshs. 500 |
| - Buying and selling of fish | Women | Kshs 500 |
| - Livestock marketing | Men | Kshs. 10,000 |
| - Boda boda taxis | Men | Kshs. 3,000 |

##### Key Outcomes of the Livelihood and Gender Participation Analysis

- Brick-making is the leading economic activity in the water supply area

- Activities that require a large capital outlay are done by men, while women undertake low profile economic activities i.e. Selling of fish and vegetables, buying and selling of cereals etc

- The most risky business is livestock marketing due frequent cases of stolen cattle. One can easily purchase stolen livestock therefore losing money.

- Bodaboda taxis business is dominated by young men and members have to purchase uniform and pay membership fee to operate

### Priority Ranking of Socio Economic Parameters

Community Ranking/Priority of Problems in the Nambale Water Supply Area.

- Inadequate water supply

- Poor road network and non-existent storm water drainage

- Low income

- Inadequate sanitation and poor environment

- Diseases

- Inadequate infrastructure in schools to address the challenges of free-primary education

- Lack of electricity

# EXISTING WATER SUPPLY SYSTEM

## General

Nambale Township is primarily served by groundwater sourced from 6 nr boreholes. However, only 2 nr boreholes are presently operational. The area covered by the water supply system is approximately 4km2.

The average yield from the 2nr operating boreholes is 6m3/hr each, giving a total daily yield of 288m3 for 24 hour pumping.

Layout plans of the Extent of Water Supply Area and the Water Supply System, including boreholes, distribution mains and storage tanks, are given in Figures 2.1 and 2.2 on pages 2-2 and 2-3 respectively.

## System Components

### Source

The water source for Nambale Town is 6nr boreholes situated within the Town. Details of the boreholes are given in Table 2.1 below.

Table 2.1 Boreholes – Details and Present Status

|  | B/Hole No. | Location Sunk | Present Status | Present Yield | Pump Details | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Not Available | ACK Compound | - Operational - Has a working Meter | 6m3/h | Make: STORK Q: 6m3/h H: 84m | Install New pump and control panel |
| 2 | C-7542 | Health Centre | - Operational - Has a working Meter | 6m3/h | Make: STORK Q: 8m3/h H: 60m | Install New pump and control panel |
| 3 | Not Available | Nambale High School | Not Operational | - | Not Equipped | Install Borehole Equipment |
| 4 | C-5188 | Divisional Headquarters | Abandoned | - | - | Drill and equip new borehole |
| 5 | Not Available | Nambale Urban Primary School | Not Operational | - | Abandoned. Stuck drill bit. | Drill and equip new borehole |
| 6 | Not Available | St Mary’s DEB Primary School | Not Operational Newly drilled (2005). Yield 7.2m3/h |  | Not Equipped. | Install Borehole Equipment |

### Storage Tanks

A total of 4nr Elevated Storage Tanks exist within the Distribution System. Details of the Tanks and their present status are given in Table 2.2

Figures 2.1 Extent of Water Supply Area

Figures 2.2 Water Supply System

| Table 2.2: Storage Tanks – Components and Present Status |  |  |
| --- | --- | --- |
| COMPONENTS | EVALUATION | REMARKS/ REHABILITATION WORKS |
| Nambale Storage Tanks 4nr tanks: - 50m3 Elevated Steel Tank - 12m3 Elevated Steel Tank - 23m3 Elevated Plastic Tank - 24m3 Elevated Plastic Tank Locations of Tanks - 50m3 and 12m3 Elevated Steel Tanks located at the Divisional Water Office - 23m3 and 24m3 Elevated Plastic Tanks located at Nambale High School Supply to Tanks The Health Centre Borehole pumps into the 50m3 and 12m3 Storage Tanks. The ACK Borehole pumps directly into the Distribution System. | - 50m3 and 12m3 Tanks operational. In good condition. - 23m3 and 24m3 Tanks not operational. Not connected to any source. | - Install Chlorination arrangements at existing tank sites. (Water presently distributed without chlorination.) - Increase storage capacity by installation of new elevated tanks, total capacity 200m3. |

The locations of the 50m3 and 12m3 elevated steel tanks are shown in Figure 2.2 on page 2-3.

### Distribution System

The existing distribution system within Nambale Town comprises approximately 11.4km of pipes ranging in diameter from 100mm to 32mm. it covers an area of approximately 4km2.

A layout plan of the distribution system is given in Figure 2.2 on page 2-3. Details and present status of the distribution system are given in Table 2.3 below.

| Table 2.3 Distribution System – Components and Present Status |  |  |
| --- | --- | --- |
| COMPONENTS | EVALUATION | REMARKS/ REHABILITATION WORKS |
| - Area of coverage: 4km2 - Pipe sizes: 32mm dia – 770m 50mm dia – 7615m 63mm dia – 850m 75mm dia – 325km 100mm dia – 1820m - The Water Distribution System is divided into two zones as follows: - Zone 1, supplied by the Health Centre Borehole. This borehole serves the adjacent areas, with a 50mm dia uPVC Main running towards the ACK church compound. Areas served by this borehole include the Nambale Divisional Headquarters, Youth Polytechnic and some premises on the Busia – Mumias Road. - Zone 2, supplied by the ACK Borehole. It includes the area around the ACK premises, the Nambale Primary and High schools, Nambale Trading Centre and some premises on the Busia – Mumias Road - The two zones are linked by a 100mm sectional valve at the Divisional Headquarters. This valve is normally closed. | - Existing pipes in the Distribution System are generally in good condition. - Approximately 10nr chambers are in poor structural condition and lack covers | - Install zonal bulk meters - Install Isolating valves - Rehabilitate broken chambers and install missing covers, marker posts etc. - New distribution and service mains for consumer connections to be laid - Install consumer water meters |

# ENVIRONMENTAL AUDIT OF EXISTING WATER SUPPLY SYSTEM

An Environmental Audit has been carried out for the Nambale Water Supply System. The environmental audit is summarized in Table 3.1.

Table 3.1 Environmental Audit for Nambale Water Supply System

| Facility/Activity Description | Observation | Environmental Impact | Mitigation measures |
| --- | --- | --- | --- |
| - Administration Compound | - Signboard: present at gate - Lighting: 2No Security lights present; 1No working - Security: 24hr security provided by Administration Police - Fence: barbed wire has been vandalised in some sections - Cleanliness: site well maintained - Sanitation facility: 1No pit latrine and bathroom present but not in use. Structure has no doors | - Easy access for unauthorized persons and domestic animals to the works. | - Repair/ replace fence |
| - Offices and Pump house - Pumphouse - Main Office - Billing & Maintenance - Store | - Structure: in average condition. Roof leakage observed - Security: Pump house has wooden door, lockable. - Lighting: 1No fluorescent light present. - Ventilation: 3No windows, all broken; adequate - Fire fighting equipment: none - First Aid Equipment: None - Frequency of cleaning: Cleaning carried out regularly General Remarks - Storage of old roof tiles, meters, old disused ‘Leeflow‘ pump and plumbing spares stored on the floor - Ventilation: 3No windows, adequate - Security: door lockable - Structure: in good condition, roof sheets damaged in some sections - Ceiling boards loose - Ventilation: 3No windows, adequate - Security: wooden doors, lockable. No grill on windows and doors - Structure: in good condition - Security: lockable door, inadequate - Tools haphazardly placed on floor | - Safety hazard in case of fire - Health hazard to staff in case of injury - Safety hazard to staff - Safety hazard to staff | - Fire extinguishers to be provided and regularly serviced - First aid equipment to be provided - Floor to be kept clear of unnecessary materials. - Repair/ replace ceiling boards |
| - Staff Housing | - Structure: 2No units, each comprising of 2No. houses; in good condition - Electricity: no supply - Water supply: present - Security: compound guarded 24hrs. Most doors and windows broken - Fence: compound fenced and separated from the administration compound - Sanitation: 2No septic tanks, 1No in poor condition. Farming carried out around tank and soakpit - Solid waste disposal: collected and burnt in a pit | - Health and safety hazard | - Farming to be stopped next to septic tank. Repair of tank to be carried out |
| - Boreholes | - 2No operational. - Metal covers for chamber present and lockable - Chambers filled with debris |  |  |
| - Chambers | - Structures in good condition - 5No chambers have broken cover slabs, missing covers and marker posts - All chambers filled with debris | - Open chambers are a safety hazard | - Repair broken chambers |
| - Storage Tanks | - 2No elevated steel tanks of 12m3 and 50m3 at administration compound. 2No elevated Polyethylene tanks at Nambale High School - Tower structure in good condition - All tanks in good condition - Access: metal ladders present and in good condition - Washout: Via pipe discharging around the tank |  |  |
| - Distribution | - Mainly consists of µPVC pipes - No bursts reported in the system - Main cause of damage is due to vehicular loading |  |  |

# EXISTING SANITATION SYSTEM

Nambale Town has no Water Borne Sanitation System in place. Most households rely on on-plot sanitation facilities, predominantly pit latrines. The pit latrines are generally around 6m deep. Households also use water from shallow wells which are on the average around 6m deep. It was reported that a shallow well in Town was recently sealed due to an outbreak of Typhoid.

The hospital, District Officer’s residence, and Ministry of Water and Irrigation Staff Houses have septic tanks.

# DEMOGRAPHIC TRENDS AND FUTURE WATER DEMAND

## Demographic Trends

Demographic trends from Central Bureau of Statistics (CBS), for 1969, 1979, 1989 and 1999 have been analysed to establish trends in terms of population size and intercensal growth rates at the National, Provincial, District and Municipality level, to develop future population projection patterns in the Municipality and its immediate environs.

Table 5.1 gives details of the intercensal demographic data and intercensal growth rates, at National, Provincial, District and Municipality / Township levels.

Table 5.1 – Intercensal Growth Rates – National, Provincial, District and Municipality

Level

|  | Indicator | 1969 | 1979 | 1989 | 1999 |
| --- | --- | --- | --- | --- | --- |
| 1. | National Population Intercensal Growth Rate | 10,942,705 - | 15,327,061 3.37% | 21,443,836 3.6% | 28,686,607 2.91% |
| 2. | Provincial Population Intercensal Growth Rate | 1,328,298 - | 1,832,663 3.22% | 2,544,329 3.28% | 3,358,776 2.78% |
| 3. | District Population Intercensal Growth Rate | 200,486 - | 297,841 3.96% | 401,658 2.99% | 370,608 (1) |
| 4. | Nambale Township Population Intercensal Growth Rate | - - | - - | 15,962 - | 22,045 3.23% |

Note: (1) – District Area Reduced from 1652km2 to 1124km2

Nambale Town was formed in the late 1980’s. Population data for Nambale Town is available for intercensal period 1989 to 1999. The intercensal growth rate during this period was 3.23%.

The population density in 1999 within the Township area of 74km2 was 297 persons per km2. However, approximately 40% of the Town population is resident in a 10km2 strip area along the Busia Mumias Road which traverses through the Town. The density in this area is around 1000 persons per km2.

The town has no industry or socio economic activity that could enhance growth in future. It is expected to grow nominally in line with trends for other urban centers within rural areas.

The intercensal growth rate for other Towns within Western Province and neighboring Province of Nyanza and Rift Valley are given in Table 5.2

Table 5.2 – Population and Intercensal Growth Rates In other Towns

| Urban Center | Population Size |  |  | Intercensal Growth Rate (%) |  |
| --- | --- | --- | --- | --- | --- |
|  | 1979 | 1989 | 1999 | 1979/1989 | 1989/1999 |
| Nakuru | 92,851 | 163,927 | 231,262 | 5.68 | 3.44 |
| Kericho | 29,603 | 48,511 | 93,213 | 4.94 | 6.53 |
| Nanyuki | 18,986 | 24,070 | 49,330 | 2.37 | 7.18 |
| Kapsabet | 2,945 | 10,537 | 48,729 | 12.75 | 15.31 |
| Kitale | 28,327 | 56,218 | 86,282 | 6.85 | 4.28 |
| Eldoret | 50,503 | 111,882 | 197,449 | 7.95 | 5.68 |
| Kisumu | 152,643 | 255,381 | 322,734 | 5.15 | 2.34 |
| Kakamega | 32,025 | 63,796 | 74,115 | 6.89 | 1.50 |
| Bungoma | 25,161 | 37,856 | 66,551 | 4.08 | 5.64 |
| Webuye | - | 40,701 | 55,398 | - | 3.08 |
| Mumias | - | 81,892 | 105,466 | - | 2.53 |
| Busia | - | 31,662 | 44,880 | - | 3.49 |
| Nambale | - | 15,962 | 22,045 | - | 3.23 |

## Potential for Physical Growth

Nambale Town is primarily a small urban center with some retail shops, schools, mission, health center and police station. The Town has no designated growth activity which could ensure major growth in the future.

In future the existing developed areas will remain the focus of development. According to the analysis of potential of these areas, it is evident that they are capable of accommodating a substantial proportion of new growth both in population and economic activity.

## Population Projections and Distribution

The population trends in the Township have been influenced by trends in fertility, mortality and migration levels and patterns as well as the national socio-economic development momentum. Population projections for the future have been carried out considering the following factors:

- Percentage intercensal global growth rates within the Province, District and Municipality

- The dynamics of land use and trends of development in each sub-location of the Municipality

- The correlation of water demand and income/type of housing, density etc.

The population trends have been analysed based on projecting the Town’s population at three variants - High, Medium and Low growth rates.

- The high variant has assumed a growth rate of 4.5%. The urban growth rate projected under the Millennium Development Goals (MDG’s) by 2015 is 4.2%. However for Kakamega Municipality this is only achievable if large scale industrialization takes place and socio-economic development of the populace is enhanced accordingly.

- The medium variant has assumed a growth rate of 2.5%. This is most likely growth rate in the long term if the adverse effect of HIV / AIDS is limited and controlled in future.

- The low variant utilizes a growth rate of 1.5% (This is the intercensal growth rate for 1989/1999 which has significantly declined due to the impact of HIV / AIDS). This scenario will pertain if the adverse impact of HIV / AIDS is not mitigated in the future.

The population data at sub location level has been obtained from Central Bureau of Statistics for 1999. This data has been projected at growth rates under three variants of High, Medium and Low for comparison purposes. The projected population up to year 2025 is given in Table 5.3.

The Sub Locations are shown in Figure 5.1 on page 5-3.

Figure 5.1 Nambale Township Sub Locations

Table 5.3 - Population Projections at Sub Location Level – Nambale Township

| Sub Location |  | 1999 | 2005 | 2010 | 2015 | 2020 | 2025 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High Variant | 4.5% |  |  |  |  |  |  |
| Siekunya |  | 5084 | 6660 | 8340 | 10445 | 13080 | 16381 |
| Nambale Township |  | 10775 | 14115 | 17676 | 22137 | 27722 | 34717 |
| Kisoko |  | 6186 | 8103 | 10148 | 12709 | 15915 | 19931 |
| Total |  | 22045 | 28878 | 36165 | 45290 | 56718 | 71029 |
| Medium Variant | 2.5% |  |  |  |  |  |  |
| Siekunya |  | 5084 | 5907 | 6693 | 7584 | 8594 | 9739 |
| Nambale Township |  | 10775 | 12519 | 14186 | 16074 | 18215 | 20640 |
| Kisoko |  | 6186 | 7187 | 8144 | 9228 | 10457 | 11850 |
| Total |  | 22045 | 25613 | 29023 | 32887 | 37266 | 42228 |
| Low Variant | 1.5% |  |  |  |  |  |  |
| Siekunya |  | 5084 | 5563 | 5996 | 6463 | 6966 | 7509 |
| Nambale Township |  | 10775 | 11790 | 12708 | 13698 | 14765 | 15914 |
| Kisoko |  | 6186 | 6769 | 7296 | 7864 | 8476 | 9137 |
| Total |  | 22045 | 24121 | 26000 | 28025 | 30207 | 32560 |

## Population Distribution

The population distribution within the Town has been classified into the following categories by Central Bureau of Statistics

Type 1		-	Rural setup within the municipality

Type 2 		-	Urban

Type 3		-	Peri Urban

The population data obtained from CBS is at Enumeration Area level and indicates the population distribution into each of the above categories.

Each settlement type has been further categorized by income groups based in data collected under the socio-economic task of this Study and by field visits to evaluate and access the income groups prevalent in specific areas of the Municipality.

The proportion of population distribution by income groups in each of the settlement categories is as follows:

Table 5.4 – Population Distribution – Nambale Town

| Type of Settlement | CBS Code | High | Medium | Low |
| --- | --- | --- | --- | --- |
|  |  | Income (Kshs.) > 25,000 p.m. | Income (Kshs.) 10,000 – 25,000 p.m. | Income (Kshs.) < 10,000 p.m. |
| Rural setup | 1 | 5% | 20% | 75% |
| Urban | 2 | 30% | 50% | 20% |
| Peri Urban | 3 | 10% | 40% | 50% |

The proportion of projected population for each income group has been distributed in each enumeration area. Overall, the population distribution for Nambale Town is analysed to be as follows:

- 11% population is categorized as High Income

- 40% population is categorized as Medium Income

- 49% population is categorized as Low Income

## Future Water Demand

### Methodology

Water demand is defined as the volume of water different categories of consumers can afford to consume in a context of unrestricted supply. The water demand of a Municipality is dependent on the climate, economic considerations, sanitation facilities, and industrial requirements.

The future water demand involves estimating the overall demand of the supply area for the present year 2005 and the long term requirements up to the year 2025. This chapter outlines the water demand evaluation for different categories of consumers based on the recommended water consumption criteria.

The water demand in the supply area has been classified into five categories as follows:

- Residential

- Institutional

- Commercial

- Industrial

The spatial distribution of the water demand within the Town is largely dependent on the land use, density and spread of the population.

The residential water consumption can be categorized into the following three main user groups based in incomes, housing density and mode of supply:

| Income group | Type of Housing | Mode of Supply |
| --- | --- | --- |
| High Income | Low density | always connected / metered water supply |
| Medium Income | Medium density | always connected / metered water supp/y |
| Low Income | High density | always connected / metered water supp/y |

During the preliminary studies for UfW, it has been determined that the current and historical billing records are unreliable and not representative of actual consumption, primarily because:

- Nearly 80% of the metering records are estimated as the meters are faulty.

- The number of Non-active connections is very high. This is primarily a result of unreliable water supply.

As a result of the above,

- Economic methods using demand functions on the basis of registered consumption can not be used to estimate the future demand. Instead an analytical approach has been used involving estimation of water demand by different categories of customers with specific consumption demand behaviors and requirements.

Total demand	=	Domestic demand + Institutional demand + Commercial

demand + Industrial demand + Unaccounted for Water

+ Treatment Works losses

The demand of each category of customer can be written as follows:

Domestic demand	= ∑Ri x Pi x Di + ∑(1-Ri) x D’i

with

i		= type of housing

Ri		= % of housing i connected to the network

Pi		= population living in type of housing i

D’i		= per capita demand of population in type of housing i connected to

the network

D’i		= per capita demand of population in type of housing i not connected to

the network

Institutional demand 	=	Demand of health sector + Demand of educational sector

+ Demand of other public services

= (IDH + IDE + IDO) x P

with

P		= Population

IDH		= Per capita demand for health sector

IDE		= Per capita demand for education sector

IDO		= Per capita demand for other public services

The per capita demand for each category of consumer has been based on the parameters for urban municipalities, set out in the MWI Design Manual (1986). These parameters have been compared with recent water demand studies carried out for other urban municipalities viz; Eldoret, Mombasa, etc. and have been found to compare reasonable well with them.

### Supply Area

The principal supply area for Nambale Town covering an area of 10km2, is designated a “growth center” within the framework of national urban strategy.

For estimation of water demand, the water supply area is defined as the current area of Nambale Town along the Busia Mumias Road which is the focus of activity and location of institutions like schools, health centers and a police station.

### Water Demand

### Residential Water Demand

The per capita demand for residential consumers is dependent on the income levels, density of housing, sanitary equipment and water consuming facilities - garden, carwash, etc. Considering the water use requirements but without restriction of supply, the overall residential water demand has been calculated based on the following per capita demand for each category of consumer:

| Income group | Mode of supply | Demand (litres/capita/day) |
| --- | --- | --- |
| High Income | always connected / metered water supply | 120 |
| Medium Income | always connected / metered water supp/y | 90 |
| Low Income | always connected / metered water supp/y | 60 |

It has been assumed that the per capita demand by type of housing will remain constant over the design period. However, the distribution of the population based on the income groups is most likely going to vary in the future due to the economic related factors. Based on past trends in Nairobi and other urban municipalities, the percentage of the population in the low income groups will probably increase, whereas the percentage of the population in the medium and high income groups will decrease slightly.

### Institutional Water Demand

- Health Sector

An inventory of existing facilities has been compiled from existing data and updated after discussion with the District Medical Officer of Health

According to the Ministry of Health (MOH) the following targets have been set for hospital beds and medical facilities based on the population to be served:

- 0.9 hospital beds per 1000 persons by the year 2010

- another 0.5 beds per 1000 persons to be available at health centers and other facilities

- a population of 50,000 to 100,000 should have a health center,

- a population of 5000 to 10000 should be served by a dispensary

The current water demand for the health sector has been determined using the following criteria as set out in the MWI Design Manual (1986):

Regional Hospital		-	400/bed/day

District Hospital		-	200/bed/day

Outpatients			-	20 /patient

Health Centre		-	5 m3/center/day + 100 //bed/day

Dispensaries		-	5 m3/center/day

Nursing Homes		-	200 l/bed/day

The calculated water demand when expressed as a per capita demand based on the total population works out in the range of a 2 l/capita/day

- Education Sector

An inventory of the existing education facilities has been compiled from existing data from both the District and Municipal Education offices.

School attendance has been estimated from the demographic data (population in age of attending school) and from enrollment rates information collected.

The water demand for the education sector has been calculated on the basis of the following criteria recommended under the MWI Design Manual (1986):

Primary / Secondary day schools 	-	25 l/students/day

Boarding 				-	50 l/student/day

The calculated water demand when expressed as a per capita demand based in the total population works out in the range of 4 l/capita/day

- Other Public Services

The public services include the local government operational services for social amenities such as the fire service, parks, markets, etc. Also included are the Technical institutes, Training centers, Police and Prisons.

An average demand of 7 l/capita/day has been adopted to cover for the public services sector. As Kakamega is the Provincial Headquarters it is necessary to allow for demand arising due to regional requirements in view of additional staff and services required.

An overall demand on 10.5 l/capita/day has been taken in the calculation of demand from the public service sector.

### Industrial Water Demand

Nambale has no major industries. Economic activity in the area is primarily of commercial nature arising from an agriculture setup in the areas surrounding the Township.

The commercial activity is dominated by small scale enterprises engaged in trade and services. These enterprises mainly consist of small shops offering a variety of goods and services for the general needs of the Town and the peri-urban inhabitants. It is assumed that the future increase in commercial activity is likely to be associated with the growth in the population of the Township.

The commercial and industrial demand is estimated to be 10% of the overall domestic demand.

### Overall Water Demand

The overall water demand of the Nambale Town (Service Area - Maximum 10km2) has been estimated for the year 2005 and the long term requirements up to the year 2025 based on the population growth series analysed in Section 6.3 of this report. The following Scenarios with different growth rates have been used in estimating the overall future water demand for the Municipality:

- High Scenario: -

Under this scenario the population is projected to grow at rate of 4.5% per annum

- Low Scenario: -

Under this scenario the population is projected to grow at rate of 1.5% per annum

- Median Scenario: -

Under this scenario the population is projected to grow at rate of 2.5% per annum

Details of the forecasted overall water demand based on the three scenarios are summarized in Table 5.5

| Table 5.5 - Overall Demand in Nambale Town Service Area (m3/day) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Category |  | 2005 | 2010 | 2015 | 2020 | 2025 |
| High Variant - 4.5% Growth Rate |  |  |  |  |  |  |
| Population |  | 9439 | 11821 | 14804 | 18539 | 23217 |
| Domestic Water Demand |  | 742 | 929 | 1164 | 1457 | 1825 |
| Health/ Education/ Institution |  | 156 | 195 | 244 | 306 | 383 |
| Commercial/ Industrial | 10% | 74 | 93 | 116 | 146 | 182 |
| Unaccounted for Water - 25% | 25% | 243 | 304 | 381 | 477 | 598 |
| Treatment Works Losses - 5% | 5% | 61 | 76 | 95 | 119 | 149 |
| Total Water Demand |  | 1276 | 1597 | 2001 | 2505 | 3137 |
| Medium Variant - 2.5% Growth Rate |  |  |  |  |  |  |
| Population |  | 8372 | 9487 | 10750 | 12181 | 13803 |
| Domestic Water Demand |  | 624 | 746 | 845 | 957 | 1085 |
| Health/ Education/ Institution |  | 129 | 157 | 177 | 201 | 228 |
| Commercial/ Industrial | 10% | 62 | 75 | 84 | 96 | 108 |
| Unaccounted for Water - 25% | 25% | 204 | 244 | 277 | 314 | 355 |
| Treatment Works Losses - 5% | 5% | 51 | 61 | 69 | 78 | 89 |
| Total Water Demand |  | 1069 | 1282 | 1453 | 1646 | 1865 |
| Low Variant - 1.5% Growth Rate |  |  |  |  |  |  |
| Population |  | 7885 | 8499 | 9160 | 9874 | 10643 |
| Domestic Water Demand |  | 620 | 668 | 720 | 776 | 837 |
| Health/ Education/ Institution |  | 130 | 140 | 151 | 163 | 176 |
| Commercial/ Industrial | 10% | 62 | 67 | 72 | 78 | 84 |
| Unaccounted for Water - 25% | 25% | 203 | 219 | 236 | 254 | 274 |
| Treatment Works Losses - 5% | 5% | 51 | 55 | 59 | 64 | 68 |
| Total Water Demand |  | 1065 | 1148 | 1238 | 1334 | 1438 |

### Recommendations

It is recommended that the overall water demand for the Service Area of Nambale Township be based in the Medium Forecast as it is the most plausible and the distribution of the population is based on trends that are most likely to be followed in the long term.

Based on the Medium Forecast the overall water demand at the design horizons is as follows:

- Present Year 2005 	-	1,069m3/day

- Year 2025		-	1,865m3/day

# PROJECT GOALS

## Development Goal

The agreed long term (2025) Development Goal of the Kenyan-German Co-operation in the project area is to ensure sustainable provision of safe and sufficient water and sanitation services for the urban population in selected towns in an economically, ecologically and socially viable and sustainable manner.

The resultant effect of the improved water and sanitation services will contribute to improvement of the health of the urban population by reducing water borne diseases and enhance economic development in the region.

## Project Objective

The objective of the project is to fulfill the agreed long term development goal in selected Towns in the Nzoia Cluster to be covered in two phases as follows:

- Phase II -  Kakamega, Busia and Nambale

- Phase III - Mumias, Butere, Kimilili, Malakisi, Kapenguria and Makutano.

The proposed project results have been defined to satisfy this objective and indicators selected to measure the achievement of the project objective. The indicators selected are as follows:

- Improvement in water supply and sanitation services by ensuring the achieved water production and sanitation system utilization meets the full design capacities of the water supply and sanitation systems.

- Reduction of Unaccounted for Water (UfW) to 25%

- Improvement in revenue collection efficiency to 98%

- Ensuring drinking water quality meets Ministry of Water & Irrigation and World Health Organisation Standards

- Ensuring treated wastewater effluent quality meets Ministry of Water & Irrigation, National Environmental Management Authority (NEMA) and World Health Organisation Standards

- Ensuring full recovery of operational costs for water supply and sanitation services

Table 6.1 shows a matrix of the indicators to be used in measuring the achievement of the project objective and their target levels for the medium term (2009) and long term (2025).

Figure 6.1 Indicators Matrix

## Target Groups and Priorities

## Target Groups

The Ultimate Target and beneficiaries of the Project is the population of the selected Towns in the Nzoia Cluster who will receive and pay for a sustainable and economically viable water supply service and have access to adequate sanitation facilities.

The current situation indicates that only about 50% of the population in the towns are served by the existing water supply systems and less than 50% of the connections in the served area are active. Therefore, less than 25% of the population in the project area presently have access to piped water supply. The rest of the population either rely on traditional sources, obtain water from neighbours or purchase water from vendors often at prices higher than those charged for piped connections.

It is mainly the population in low cost housing and informal settlements that is currently forced to use alternative water sources. Improved service standards and coverage will directly benefit this element of the target group.

Furthermore, as the responsibility for collecting water traditionally falls on the female members of the household, improved levels of service and coverage will reduce the time taken by women to collect water and, consequently, increase the time available for productive work. This will contribute to reducing poverty levels in the project area.

Commercial water users are another important target group, as increased availability and reliability of water supply services will contribute to realizing the potential for increased economic activity in the project area.

The intermediate target groups are organizations newly established in the project area in accordance with the Water Act, 2002, namely the Water Service Board and the Water Service Provider. These organizations will be provided with access to investment funds for rehabilitation of existing facilities and for expansion of facilities to increase coverage of services in line with the Development Goal indicators.

## Priorities

The selection of priorities for investment support has been based on a number of factors as follows:

- Potential commercial viability

- Potential for the impact of an improved level of service delivery on the greatest number of consumers in the short term

- The basic soundness of existing infrastructure and operational and management systems

- Perceived willingness to combine service management on a cluster basis for improved cost effectiveness, in accordance with the Water Act and National Water Services Strategy

- Geographical proximity for more cost effective management

- Maximum potential impact of initially available investment funds.

# WATER AND SANITATION SERVICE PROVIDERS

Under the Water Act 2002, the Water and Sanitation Schemes for the Phase II Towns of Kakamega, Busia and Nambale fall within the Lake Victoria North Water Services Board (LVNWSB), who in turn are required to appoint Water Service Providers (WSP’s) to operate and maintain these systems in each Town.

The present status regarding the management of the Water and Sanitation Systems in Nambale is as follows:

The Nambale Water Supply System is being managed by the District Water office of Ministry of Water and Irrigation. The revenue collected is transferred to MWI who are responsible for payment of staff salaries and electricity. LVNWSB are involved in co-ordination of all activities in the Interim Period prior to appointment of a suitable Water Service Provider.

Nambale has no water-borne sewerage network in place. On plot sanitation, mainly pit latrines, is predominant in the area.

## Appointment of Water and Sanitation Service Providers

At the Inception Stage of Nzoia Cluster, it was envisaged that the 12 Towns under Phases I, II, and III will be managed by a single Water Service Provider.

Due to logistical reasons and rationalization of operations, it is possible that the Nzoia Cluster can be divided into two smaller Clusters:

- Northern Cluster comprising the seven Towns of Kitale, Bungoma, Webuye, Kimilili, Malakisi, Kapenguria and Makutano, operated by Nzoia Water and Sanitation Company Ltd. (NZOWASCO)

- Southern Cluster comprising the five Towns of Kakamega, Busia, Nambale, Mumias and Butere, operated by Western Water and Sanitation Service Company Ltd.

During a meeting held on 16th November, 2005 between LVNWSB and CES/GFA/MIBP Joint Venture, LVNWSB indicated that the Western Water and Sanitation Co. Ltd has been registered and advertisements for appointment of Directors is in hand. The Company has been registered to operate the Water Supply and Sanitation Systems for the Four Towns of Kakamega, Busia, Nambale and Mumias.

The inclusion of Butere is still to be resolved.

## Evaluation of Existing of Water and Sanitation Service Providers

The Terms of Reference of the Feasibility Study requires the evaluation of the existing Water and Sanitation Service Providers. As the appointment and establishment of the Water Service Providers is in a transition stage, LVNWSB indicated that the operation costs for the existing water supply and sanitation systems shall be estimated. In this respect the Consultants were asked to use the NZOWASCO model i.e. organisation setup for Corporate Team and Area Offices as a basis for evaluating the operation costs relating to staff.

LVNWSB also confirmed that the sanitation systems in all Towns will be operated and maintained by the Water Services Providers in accordance with the Water Act.

## Proposed Organization Setup – Western Water Service Company Ltd.

The organization setup for the Western Water Service Company including the Technical and Commercial setup at the Area Offices of Kakamega, Busia and Nambale have been developed based on the NZOWASCO model. The Technical and Commercial Staff requirements has been assessed based on the Consultants experience of operational requirements for similar schemes.

The organization setups developed are given in Figures 7.1, 7.2 and 7.3.

Figure 7.1 Organization Setup, Corporate Management Team – Western Water

Service Company Ltd

Figure 7.2 Organization Setup, Nambale Area Office – Technical Division

Figure 7.3 Organization Setup, Nambale Area Office – Commercial Division

## General Initial Assistance in Establishment of Water Service Providers (WSP)

From the problems faced by NZOWASCO in the initial stages of establishment, the following should be addressed:

- According to “Kenya Employment Act” almost all civil service employees and workers from previous State water institutions must be taken-over by the new Water Service Provider. As these institutions are over-staffed and in some cases under-staffed, economical staff labour expenses may not be achieved.

- No start-up cash-flow is available to establish basic office and workshop facilities

- Outstanding debts are very high. Governmental institutions e.g police stations, prisons, schools, etc. are not willing to pay the debts or even to authorize metering of supplies.

- Insufficient data about existing facilities especially location of water supply mains and connection details.

- Insufficient data about plot owners.

- Water laboratory should be established for continuous monitoring of water quality.

- Unauthorized collection of revenue by staff.

- Preferential services like continuous supply and full pressure given to some customers only.

### Recommendations

- The WSP should be authorized to optimize its personnel staff needs according to Technical and Administrative requirements, independently from previous state working contracts.

- The WSP shall be provided with a start-up soft-loan or grant, which shall be bound to:

- Energy expenses for first 2 years

- Chemicals expenses for first 2 years

- Purchase of necessary amount of water meters for installation in first year and tools and equipment for operation and maintenance

- Hard and software equipment

- GIS software and training

- Pick-up 4WD vehicles

- Outstanding debts and fees should not be taken-over by the WSP. A starting point with nil debts should be fixed.

- The LVNWSB and MWI must support the WSP in order to get agreements with Governmental Institutions for correct metering and payments.

- It must be ensured by LVNWSB and the relevant Municipalities that all data are made available to WSP from the very beginning.

- The LVNWSB or the WRMA must provide adequate laboratory facilities for water and sewage analysis, where the services will be charged to the WSP at reasonable prices.

- A suitable financial control system needs to be established.

- The WSP must be responsible for Water Supply and Sewerage Services from the very beginning.

- All future contracts concerning accompanying measures, capacity building or any other external support or funding should be made direct with the WSP in order to increase responsibility and to harmonize operation. The overall responsibility to be still with LVNWSB.

- In order to establish a proper sewerage system and to prevent groundwater pollution, the WSP must charge non-sewered house connections with a small service fee. From this fee, the client may get regular septic tank emptying for free. The WSP must maintain suitable exhauster equipment. Local artisans should be trained in construction of Ventilated Improved Pit Latrines, etc.

# EXISTING ASSETS

A valuation of the existing assets in the Nambale Water Supply System been carried out on the basis of current market prices. The value of the assets is shown in Table 8.1 below.

Table 8.1 Nambale Water Supply System Assets Valuation

| DESCRIPTION |  | UNIT | QTY | RATE | AMOUNT (Kshs) | AMOUNT (Euros) |
| --- | --- | --- | --- | --- | --- | --- |
| WATER SUPPLY COMPONENTS |  |  |  |  |  |  |
| 1 | Boreholes |  |  |  |  |  |
|  | BH 1 | m | 84 | 7,000.00 | 588,000.00 | 6,681.82 |
|  | BH 2 | m | 60 | 7,000.00 | 420,000.00 | 4,772.73 |
|  | BH 3 - Not Equipped | m | 80 | - | - | - |
|  | BH 4 - Not Equipped | m | 80 | - | - | - |
|  | BH 5 - Abandoned (Not Operatable) | m | 80 | - | - | - |
|  | BH 6 - Not Equipped | m | 80 | - | - | - |
| 2 | Storage Tanks |  |  |  |  |  |
|  | Elevated Steel Tank 50m3 | LS |  |  | 2,050,000.00 | 23,295.45 |
|  | Elevated Steel Tank 112m3 | LS |  |  | 1,750,000.00 | 19,886.36 |
|  | Elevated Plastic Tank 24m3 | LS |  |  | 50,000.00 | 568.18 |
|  | Elevated Plastic Tank 23m3 | LS |  |  | 50,000.00 | 568.18 |
| 3 | Distribution Mains |  |  |  |  |  |
|  | 100-32mm | m | 11,400 | 600.00 | 6,840,000.00 | 77,727.27 |
|  | TOTAL VALUE OF EXISTING WATER SUPPLY ASSETS AT PRESENT COST |  |  |  | 11,748,000.00 | 133,500.00 |
|  | BUILDINGS FOR WATER OPERATOR |  |  |  |  |  |
| 1 | Offices, Stores etc | m2 | 200 | 15,000.00 | 3,000,000.00 | 34,090.91 |
| 2 | Staff Houses - 4nr Grade 9 | m3 | 168 | 15,000.00 | 2,520,000.00 | 28,636.36 |
|  | TOTAL VALUE OF BUILDINGS AT PRESENT COST |  |  |  | 5,520,000.00 | 62,727.27 |
|  | TOTAL VALUE OF ASSETS AT PRESENT COST |  |  |  | 17,268,000.00 | 196,227.27 |

*1 Euro = 88 Kshs (Jan 2006)

# REHABILITATION MEASURES FOR EXISTING WATER SUPPLY SYSTEM

The rehabilitation works necessary to be carried out on the Nambale Water Supply System are shown in Table 9.1. The construction costs for civil and electro mechanical works have been based on market prices or derived from current on going Projects i.e. Nyeri Water Supply Project, Eldoret Sanitation Project etc.

In addition to the rehabilitation measures, it is proposed to construct a number of water kiosks in order to provide affordable access to potable water for the urban poor who are unable to afford individual water connections. In Nambale Town, 49% of the population is categorized as Low Income (see section 5.4 of this report) and 30% of this low income group has been considered as requiring water kiosks. A criterion of 600 persons per water kiosk has been adopted. The total number of water kiosks required is therefore estimated as follows:

| Year | Total Population | No. of People Requiring Water Kiosks | Number of water kiosks Required |
| --- | --- | --- | --- |
| 2009 | 29,000 | 4,200 | 7 |
| 2025 | 42,228 | 6,200 | 10 |

Table 9.1 	 Proposed Rehabilitation Measures for Nambale Water Supply System

|  | DESCRIPTION |  | UNIT | QTY | RATE (KShs) | AMOUNT (KShs) | AMOUNT (EURO'S) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A | BOREHOLES |  |  |  |  |  |  |
|  |  | - Installation of new borehole pumps and associated electrical control panel at existing 2nr boreholes | nr | 2 | 250,000.00 | 500,000.00 | 5,681.82 |
|  |  | - Drilling and equiping of new borehole | m | 80 | 15,000.00 | 1,200,000.00 | 13,636.36 |
|  |  | - Installation of electromagnetic meters, 150mm dia, on 3nr boreholes | nr | 3 | 80,000.00 | 240,000.00 | 2,727.27 |
|  |  | - Drilling and equiping of new borehole to replace abandoned borehole C-7542 | m | 80 | 15,000.00 | 1,200,000.00 | 13,636.36 |
|  | SUB TOTAL - Boreholes |  |  |  |  | 3,140,000.00 | 35,681.82 |
| B | STORAGE RESERVOIRS |  |  |  |  |  |  |
|  |  | - Installation of new elevated tanks, 2nr, 100m3 capacity each | nr | 2 | 2,462,500.00 | 4,925,000.00 | 55,965.91 |
|  |  | - Installation of chlorination arrangement at 3nr tank sites | nr | 3 | 250,000.00 | 750,000.00 | 8,522.73 |
|  | SUB TOTAL - Storage Reservoirs |  |  |  |  | 5,675,000.00 | 64,488.64 |
| C | DISTRIBUTION SYSTEM |  |  |  |  |  |  |
|  |  | - Installation of zonal bulk meters | LS |  |  | 500,000.00 | 5,681.82 |
|  |  | - Reconstruction of broken chambers and covers | nr | 10 | 15,000.00 | 150,000.00 | 1,704.55 |
|  |  | - Laying of 150mm dia ferrous distribution main | m | 2000 | 4,695.00 | 9,390,000.00 | 106,704.55 |
|  |  | - Laying of 100mm dia distribution main | m | 3000 | 3,646.50 | 10,939,500.00 | 124,312.50 |
|  |  | - Installation of 100mm dia isolating valves | nr | 8 | 250,000.00 | 2,000,000.00 | 22,727.27 |
|  |  | - Installation of marker posts | nr | 10 | 2,000.00 | 20,000.00 | 227.27 |
|  |  | - Extension of service mains for household connections 50mm to 25mm | m | 600 | 2,000.00 | 1,200,000.00 | 13,636.36 |
|  |  | - Replacement of water meters and associated fittings - 300nr | nr | 300 | 4,840.00 | 1,452,000.00 | 16,500.00 |
|  |  | Construction of Water Kiosks | nr | 5 | 150,000.00 | 1,200,000.00 | 13,636.36 |
|  | SUB TOTAL - Distribution System |  |  |  |  | 26,401,500.00 | 300,017.05 |
| D | MISCELLANEOUS EQUIPMENT AND VEHICLES |  |  |  |  |  |  |
|  |  | - Double cab pick-ups | nr | 1 | 2,500,000.00 | 2,500,000.00 | 28,409.09 |
|  |  | - Motor bikes | nr | 2 | 400,000.00 | 800,000.00 | 9,090.91 |
|  |  | - Tools and equipment for Operation and Maintenance | LS |  |  | 500,000.00 | 5,681.82 |
|  |  | - Leak detection equipment for UfW assessment | LS |  |  | 500,000.00 | 5,681.82 |
|  |  | - Office, IT and communication equipment | LS |  |  | 500,000.00 | 5,681.82 |
|  |  | - Billing software | LS |  |  | 1,320,000.00 | 15,000.00 |
|  |  | - GIS software and hardware | LS |  |  | 1,056,000.00 | 12,000.00 |
|  | SUB TOTAL - Miscellaneous Equipment and Vehicles |  |  |  |  | 7,176,000.00 | 81,545.45 |
|  | SUB TOTAL 1 |  |  |  |  | 42,392,500.00 | 481,732.95 |
|  | ADD 20% FOR PRELIMINARIES AND GENERAL ITEMS |  |  |  |  | 8,478,500.00 | 96,346.59 |
|  | SUB TOTAL 2 |  |  |  |  | 50,871,000.00 | 578,079.55 |
|  | ADD 7.5% FOR PHYSICAL CONTINGENCIES |  |  |  |  | 3,815,325.00 | 43,355.97 |
|  | SUB TOTAL 3 |  |  |  |  | 54,686,325.00 | 621,435.51 |
|  | ADD 7.5% FOR PRICE CONTINGENCIES |  |  |  |  | 4,101,474.38 | 46,607.66 |
|  | SUB TOTAL 4 |  |  |  |  | 58,787,799.38 | 668,043.17 |
|  | ADD 9% CONSULTANCY COST FOR DESIGN, TENDER DOCUMENT PREPERATION AND SUPERVISION |  |  |  |  | 5,290,901.94 | 60,123.89 |
|  | GRAND TOTAL FOR NAMBALE WATER SUPPLY SYSTEM REHABILITATION WORKS |  |  |  |  | 64,078,701.32 | 728,167.06 |

*1 Euro = 88 Kshs (Jan 2006)

# PROPOSED EXPANSION OF THE WATER SUPPLY SYSTEM

## General

The Year 2025 projected water demand for Nambale Township (Service Area 10km2) is 1865m3/d, capable of serving a population of 13,803 persons.

The present water demand is estimated to be 1,069m3/d. The average production from the 2nr boreholes presently supplying Nambale Township is 192m3/d. The system therefore requires augmentation to enable it meet the present and future water demand.

Proposals of expansion of the water supply system have been developed based on availability of sources i.e. surface or groundwater and their safe yields to meet the long term (Year 2025) water demand.

Economic comparisons of the various alternatives for expansion have been carried out to determine the most viable scheme based on capital investments, energy costs, operation and maintenance costs, operation and maintenance capacity of the water service providers and environmental impacts of the proposed measures.

In selection of the possible sources for water supply, the following basic criteria are considered:

- The capacity of the source to yield the future water demand for the area with possible consequences on the adjoining areas.

- Suitability of the source for a gravity draw off and gravity feed into the reticulation

- Capital expenditure required to develop the source, operation and maintenance costs

- Chemical composition of water and type of treatment required to make it fit for human consumption

- Easy access to the source for routine maintenance

## Surface Water Sources

Potential surface water sources within the vicinity of Nambale Town that can serve Nambale Town are:

- River Sio flowing approximately 2km south of the Town

- River Malakisi flowing approximately 20km north of the Town

River Sio has adequate low flow at 95% probability (1 in 20 year return period) and 98% probability (1 in 50 year return period) to meet the future demand for Nambale and Busia Municipality. Busia Municipality is presently served from River Sio.

The low flows of Malakisi river has to be ascertained especially since the source also serves Malakisi Water Supply including Malaba Town.

## Ground Water Potential

Hydrogeological data for Nambale Township and the surrounding areas has been collected from Ministry of Water and Irrigation and from previous studies carried out in the area (Ref KEFINCO – Rural Water Supply Development Project – Western Province 1983 – 1985)

The data has been compiled, analysed and evaluated. A summary of the boreholes drilled in the area is as follows:

- Total of 57 boreholes were drilled within a radius of about 10 kilometers with an average depth of 47.5 metres

- The mean yield is 24.5 m3/hr.

- The tested discharge rate ranges from 0 to 17 m3/hr.

- 15 boreholes dry borehole were drilled close to Nambale Town

- Two aquifers were encountered at an average of 19, and 53 metres

- Static water level averaged 2.45 metres.

Groundwater potential in this area is very low compared to the other towns.

- On the western side of the Town (Busia Mapsheet) a total of 17 boreholes Out of the 18 boreholes drilled on the eastern side (Mumias Mapsheet) of the Nambale Town 7 are dry while 9 boreholes have yields less than 1.8 m3/hr. Only two with yields of 4.6 and 17 1.8 m3/hr can be termed successful and are separated by more than 7 kilometers.

- On the north eastern part of the Town (Malakisi Mapsheet) 10 boreholes have been drilled. None of the drilled boreholes is dry but the yield of 8 boreholes is in the range of between 0.4 and 2.7 m3/hr. Two boreholes have a yield of 9 m3/hr but are separated by 6 kilometres.

- On the north western part of the Town (Tororo Mapsheet) 12 boreholes have been drilled of which 3 were dry. The rest of the 9 boreholes have yields ranging between 0.15 – 1.26 m3/hr. It is apparent that no further groundwater investigation and development should be considered in this part.

- Have been drilled in the area. Out these 5 boreholes were dry whereas the low yielding boreholes have yield ranging between 1.16 to 1.5 m3/hr. The high yielding boreholes 3 kilometres from the Town have yields ranging between 7.2 to 11.8 m3/hr. This is indicates rather a high potential.

Six boreholes located within 3 kilometres east of the Town have a cumulative yield of 1097 m3/d assuming a 20-hour pumping regime.

Further hydrogeological and geophysical investigations need to be carried out in this area to determine aquifer potential.

The location of the existing boreholes in the area is shown in Figure 10.1 on Page 10-3.

FIG 10.1 - Location of the existing boreholes

## Alternative Schemes for Expansion of Water Supply to Nambale Town

A number of alternative schemes for water supply to Nambale Town have been studied. Figure 10.2 on page 10-5 shows locations of headworks and route plans for mains for the alternative schemes studied.

Details of the Alternative Schemes are as follows:

### Alternative Scheme 1

Gravity Scheme From Malakisi River (Intake, Treatment Works, Raw and Treated Water Mains Shared with Proposed Scheme for Busia Municipality)

The proposed scheme is based on constructing a run-of-the-river intake on River Malakisi at 1420m amsl near Namangofulo Trading  Center, 10km North of Malakisi Town. The Scheme will also serve Busia Municipality which has a projected ultimate (year 2025) demand of 12,846m3/d.

Raw Water can be gravitated to the proposed treatment works site 6km away at 1380m amsl. Treated water can also be gravitated to storage tanks located in Nambale site at 1220m amsl. From the Storage Tanks treated water can be gravitated into the distribution network within the Town.

Enroute areas of Malakisi Town, Malaba Town, Amukura Trading Centre, can also be supplied by gravity under this Alternative. The supply can be extended by gravity to Busia Municipality and rural areas of Mundika and Angoromo.

Briefly the proposed Scheme comprises:

- Run-of-the-River Intake in River Malakisi at 1420m amsl (Detailed hydrological analysis has to be carried out to determine available low flow at 96% and 98% probability. If the available low flow is inadequate, impoundment will need to be considered.)

- 400mm dia ferrous pipe Raw Water Gravity Main, length 6 km

- Treatment Works, capacity 15,000m3/d (13,000m3/d for Busia, 2,000m3/d for Nambale)

- 400mm dia ferrous pipe Treated Water Gravity Main to Busia Town, length 50km

- 200mm dia ferrous pipe Treated Water Gravity Branch Main to Nambale Town, length 16km

- 1nr Storage Reservoir in Nambale Town– Capacity 1,000m3

A schematic layout plan of Alternative 1 is given in Figure 10.3 on Page 10-6

Figure 10.2  location of the intakes for the alternatives studied

Figure 10.3  Schematic layout plan of Alternative 1

Table 10.1 outlines the estimated costs of Alternative Scheme 1.

The costs of the components of the scheme that are shared by the Busia and Nambale Schemes, i.e. Intake Works, Raw Water Gravity Main, Treatment Works, and the Treated Water Gravity Main have been apportioned to each scheme by ratio of its projected ultimate (year 2025) water demand as follows:

| Scheme | Year 2025 Demand (m3/d) | Scheme’s Demand as % of total |
| --- | --- | --- |
| Busia | 12,846 | 87.3 |
| Nambale | 1865 | 12.7 |
| Total | 14,711 | 100 |

The percentage of the shared scheme components costs allocated to the Nambale Scheme is thus 12.7% of their total cost.

Table 10.1 Estimated Costs for Alternative Scheme 1

| DESCRIPTION |  | UNIT | QTY | RATE | TOTAL AMOUNT (Nambale & Busia) (Kshs) | AMOUNT ALLOCATED TO NAMBALE (Kshs) | AMOUNT ALLOCATED TO NAMBALE (Euros) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Intake on River Malakisi | LS |  |  | 2,500,000.00 | 316,939.70 | 28,409.09 |
| 2 | Raw Water Gravity Main - 400mm dia steel pipe | m | 6,000 | 10,073.70 | 60,442,200.00 | 7,662,613.21 | 686,843.18 |
| 3 | 15,000m3/d Treatment Works | m3 | 15000 | 10,800.00 | 162,000,000.00 | 20,537,692.88 | 1,840,909.09 |
| 4 | Treated Water Gravity Main - 400mm dia steel pipe | m | 50,000 | 10,073.70 | 503,685,000.00 | 63,855,110.12 | 5,723,693.18 |
| 5 | Treated Water Gravity Branch Line - 200mm dia steel pipe | m | 16,000 | 6,084.00 |  | 97,344,000.00 | 1,106,181.82 |
| 6 | Storage Tank - 1000m3 | m3 | 1,000 | 8,328.00 |  | 8,328,000.00 | 94,636.36 |
| 7 | Distribution Mains |  |  |  |  |  |  |
|  | 50-200mm | m | 5,000 | 2,768.14 |  | 13,840,694.01 | 157,280.61 |
|  | 50-25mm | m | 5,000 | 874.16 |  | 4,370,797.31 | 49,668.15 |
| SUB TOTAL 1 |  |  |  |  |  | 216,255,847.24 | 9,687,621.49 |
| Add 20% of Sub-Total 1 for Preliminaries & General Items |  |  |  |  |  | 43,251,169.45 | 1,937,524.30 |
| SUB TOTAL 2 |  |  |  |  |  | 259,507,016.69 | 11,625,145.79 |
| Add 7.5% of Sub-Total 2 for Physical Contingencies |  |  |  |  |  | 19,463,026.25 | 871,885.93 |
| SUB TOTAL 3 |  |  |  |  |  | 278,970,042.94 | 12,497,031.72 |
| Add 9% of Sub-Total 3 for Consultancy Cost for Design, Tender Document Preparation and Supervision |  |  |  |  |  | 25,107,303.86 | 1,124,732.86 |
| GRAND TOTAL FOR ALTERNATIVE SCHEME 1 |  |  |  |  |  | 304,077,346.81 | 13,621,764.58 |

*1 Euro = 88 Kshs (Jan 2006)

### Alternative Scheme 2

Pumping Scheme from Intake on Sio River

The proposed scheme is based on constructing a run-of-the-river intake on River Sio, located 2km south of Nambale Town. Raw water would be pumped to a Treatment Works located 1km from the Intake. Treated water would be pumped to elevated storage tanks in Nambale Town for gravity supply to the distribution network.

Briefly, the proposed scheme comprises:

- Run-of-the-River Intake on River Sio at 1180m amsl

- Raw Water Pumping Station

- Raw Water Pumping Main – 200mm dia ferrous pipe, length 1000m

- Treatment Works, capacity 2000m3/day

- Treated Water Pumping Station

- Treated Water Pumping Main – 200mm dia ferrous pipe, length 1200km

- 2nr elevated Storage Reservoirs – capacity 1,000m3

A Schematic Layout Plan of Alternative Scheme 2 is given in Figure 10.4 on Page 10-9

Table 10.2 outlines the estimated costs for Alternative Scheme 2.

Table 10.2 Estimated Costs for Alternative Scheme 2

| DESCRIPTION |  | UNIT | QTY | RATE | AMOUNT (Kshs) | AMOUNT (Euros) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Raw Water Intake on River Sio | LS |  |  | 2,500,000.00 | 28,409.09 |
| 2 | Raw Water Pumping Station & Pumps | LS |  |  | 2,200,000.00 | 25,000.00 |
| 3 | Raw Water Rising Main - 200mm dia steel pipe | m | 1,000 | 6,084.00 | 6,084,000.00 | 69,136.36 |
| 4 | 2000m3/d Treatment Works | m3 | 2,000 | 14,000.00 | 28,000,000.00 | 318,181.82 |
| 5 | Treated Water Pumping Station & Pumps | LS |  |  | 2,200,000.00 | 25,000.00 |
| 6 | Treated Water Rising Main - 200mm dia steel pipe | m | 1,200 | 6,084.00 | 7,300,800.00 | 82,963.64 |
| 7 | Storage Tanks - Elevated Tanks, 1000m3 | LS |  |  | 19,000,000.00 | 215,909.09 |
| 8 | Distribution Mains |  |  |  |  |  |
|  | 50-200mm | m | 5,000 | 2,768.14 | 13,840,694.01 | 157,280.61 |
|  | 50-25mm | m | 5,000 | 874.16 | 4,370,797.31 | 49,668.15 |
| SUB TOTAL 1 |  |  |  |  | 85,496,291.32 | 971,548.76 |
| Add 20% of Sub-Total 1 for Preliminaries & General Items |  |  |  |  | 17,099,258.26 | 194,309.75 |
| SUB TOTAL 2 |  |  |  |  | 102,595,549.58 | 1,165,858.52 |
| Add 7.5% of Sub-Total 2 for Physical Contingencies |  |  |  |  | 7,694,666.22 | 87,439.39 |
| SUB TOTAL 3 |  |  |  |  | 110,290,215.80 | 1,253,297.91 |
| Add 9% of Sub-Total 3 for Consultancy Cost for Design, Tender Document Preparation and Supervision |  |  |  |  | 9,926,119.42 | 112,796.81 |
| GRAND TOTAL FOR ALTERNATIVE SCHEME 2 |  |  |  |  | 120,216,335.22 | 1,366,094.72 |

*1 Euro = 88 Kshs (Jan 2006)

Figure 10.4 Schematic Layout plan of Alternative 2

### Alternative Scheme 3

Supply by pumping from Busia Treatment Works (Intake, Raw Water Main and Treatment Works Shared with Busia Water Supply Scheme)

Under this Scheme, Nambale Town would be supplied from the existing Busia Intake on River Sio and Treatment Works. Treated water would be pumped via a 200mm dia Main from the Busia Treatment Works to elevated storage tanks in Nambale Town from which it would be gravitated into the Town’s distribution system.

Briefly the proposed scheme comprises:

- Augmentation of existing Raw Water Pumping Station at the Busia Intake

- New Raw Water Pumping Main – 400mm dia ferrous pipe length 700m.

- Augmentation of existing Busia Treatment Works by 18,000m3/d (16,000m3/d for Busia including the Funyula-Bumula Scheme and 2,000m3/d for Nambale).

- Augmentation of existing Treated Water Pumping Station at Busia Treatment Works

- 200mm dia ferrous pipe Treated Water Main, length 15km, to Nambale Town

- 2nr elevated storage reservoirs in Nambale Town, total capacity 1,000m3

A Schematic Layout Plan of Alternative Scheme 3 is given in Figure 10.5 on Page 10-11.

Table 10.3 outlines the estimated costs for Alternative Scheme 3.

The costs of the components of the scheme that are shared by the Busia and Nambale Schemes, i.e. Intake Works, Raw Water Gravity Main and the Treatment Works, have been apportioned to each scheme by ratio of its projected ultimate (year 2025) water demand as follows:

| Scheme | Year 2025 Demand (m3/d) | Scheme’s Demand as % of total |
| --- | --- | --- |
| Busia (Including Funyula-Bumula Scheme) | 16,096 | 89.6 |
| Nambale | 1865 | 10.4 |
| Total | 17,961 | 100 |

The percentage of the shared scheme components costs allocated to the Nambale Scheme is thus 10.4% of their total cost.

Figure 10.5 Schematic Layout plan of Alternative 3

Table 10.3 Estimated Costs for Alternative Scheme 3

| DESCRIPTION |  | UNIT | QTY | RATE | TOTAL AMOUNT (Nambale & Busia) (Kshs) | AMOUNT ALLOCATED TO NAMBALE (Kshs) | AMOUNT ALLOCATED TO NAMBALE (Euros) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Augmentation of Raw Water Pumping Station & Pumps | LS |  |  | 16,000,000.00 | 2,028,414.11 | 23,050.16 |
| 2 | Raw Water Rising Main - 400mm dia steel pipe | m | 700 | 10,073.70 | 7,051,590.00 | 893,971.54 | 10,158.77 |
| 3 | Augmentation of Busia Treatment Works by 18,000m3/d | m3 | 18,000 | 10,800.00 | 194,400,000.00 | 20,185,735.76 | 229,383.36 |
| 4 | Augmentation of Busia Treated Water Pumping Station & Pumps | LS |  |  |  | 6,494,400.00 | 73,800.00 |
| 5 | Treated Water Rising Main - 200mm dia steel pipe 15km long | m | 15,000 | 6,084.00 |  | 91,260,000.00 | 1,037,045.45 |
| 6 | 2nr Elevated Tanks, 1000m3 | LS |  |  |  | 19,000,000.00 | 215,909.09 |
| 7 | Distribution Mains |  |  |  |  |  |  |
|  | 50-200mm | m | m | 5,000 | 2,768.14 |  | 13,840,694.01 |
|  | 50-25mm | m | m | 5,000 | 874.16 |  | 4,370,797.31 |
| SUB TOTAL 1 |  |  |  |  |  | 157,545,214.04 | 1,790,286.52 |
| Add 20% of Sub-Total 1 for Preliminaries & General Items |  |  |  |  |  | 31,509,042.81 | 358,057.30 |
| SUB TOTAL 2 |  |  |  |  |  | 189,054,256.84 | 2,148,343.83 |
| Add 7.5% of Sub-Total 2 for Physical Contingencies |  |  |  |  |  | 14,179,069.26 | 161,125.79 |
| SUB TOTAL 3 |  |  |  |  |  | 203,233,326.11 | 2,309,469.61 |
| Add 9% of Sub-Total 3 for Consultancy Cost for Design, Tender Document Preparation and Supervision |  |  |  |  |  | 18,290,999.35 | 207,852.27 |
| GRAND TOTAL FOR ALTERNATIVE SCHEME 3 |  |  |  |  |  | 221,524,325.45 | 2,517,321.88 |

*1 Euro = 88 Kshs (Jan 2006)

### Alternative Scheme 4

Supply from Boreholes - Augmentation of Existing Water Supply System

The existing water supply system in Nambale Town is a ground water system consisting of 6nr boreholes, of which only 2nr are presently operational. Augmentation of the existing groundwater supply system has been considered as an option for the expansion of water supply to the Town. The findings of a groundwater potential evaluation study and details of the proposed groundwater supply scheme are given below.

- Study of Groundwater Potential in the Nambale Area.

In a previous pre-feasibility study of groundwater potential in the area, a few boreholes in Nambale Town consistently indicated a higher groundwater potential compared to the areas in the vicinity of the Town where the existing production boreholes are located.

As a follow-up to this pre-feasibility study, a detailed evaluation of the groundwater potential of the area was carried out. The borehole site investigations were carried out using a multi-step approach as follows:

- Collection of the hydrogeological information from the previous studies carried out by KEFINCO from the Busia Water Office, particularly test pumping data, which was not available during the pre-feasibility study of the area.

- Execution of geophysical sounding within the interpreted aquifer to determine its morphology (geometry and thickness).

- Compilation, analysis and evaluation of the gathered data and information.

The findings of the groundwater evaluation study are summarised below.

A review of the existing boreholes drilled in the area was carried out, having obtained data from the Busia Water Office. The results of the review are summarised below:

Table 10.4 Data for Existing Boreholes in the vicinity of Nambale Town

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| BH No. | Borehole | Depth | WSL | SWL | Q | Drawd. | Sp.Cap. |
| C- | Owner | (m) | (m bgl) | (m bgl) | (m3/hr) | (m) | (m3/hr/m) |
| 5151 | Min. of Water | 55 | 21, 33-50 |  | 7 |  |  |
| 5188 | County Council Busia | 52 | 19, 35-50 | 7.68 | 10.87 | 11.29 | 0.963 |
| 5929 | Busibinaho Sch. | 40 | 28 - 34 | 4.83 | 1.5 | 1.76 | 0.852 |
| 5930 | Nasira Sch. | 55 | 39 - 48 | 11.68 | 1.38 | 0.58 | 2.379 |
| 5931 | Nasira RC School | 45 | 10-14, 25-35 | 9 | 1.44 | 1.0 | 1.44 |
| 7539 | Tangakama village | 46 | 10 - 11 | 4 | 0.83 |  |  |
| 7540 | Katikoko Village | 49 | 28 - 32 | 9 | 9.5 |  |  |
| 7541 | Nambale Water Supply | 78.4 | 50 | 9 | 6.99 | 10.72 | 0.652 |
| 7542 | Nambale Water Supply | 68 | 42 | 9 | 12.41 | 20.16 | 0.616 |
| 8354 | KEFINCO | 43 | 12 – 14, 23 - 30 | 4 | 2.03 | 27.43 | 0.074 |
| 9614 | Min. of Water | 34 | 10, 16 | 9.7 | 7.2 |  |  |
| 10983 | Sulwe | 46 | 33,38 | 9.66 | 9 |  |  |
| 11797 | Brige E.B. Sifuma | 56 | 26 | 3 | 14.4 | 25 | 0.576 |
|  | ACK Church | 43 | 16 | 8 | 16 | No DD | Above 14.4 |
|  | Nambale Sec. Sch. | 44 |  |  | 6.5 |  |  |
|  | Nambale Urban Pri. Sch. |  |  |  | Dry |  |  |
|  | Average (available data) | 50 | 14, 30-42 | 5.5 | 5.8 | 12.24 | 0.944 |

Notes referring to Table 10.4:

- Ministry of Water and Irrigation Borehole Identification Number

- Borehole Owner (Distance in km , and direction from proposed drilling site)

- Total drilled depth in meters below ground level

- Water Struck Levels in m bgl

- Static Water Level, depth of piezometric surface, or water table, in m bgl

- Tested yield in m3 /hr (not necessarily equal to sustainable yield)

- Drawdown (m)

- Specific capacity: the ratio of yield and drawdown, or the discharge per metre drawdown

- A total of 16 boreholes have been drilled in the Nambale Centre aquifer. 9 of these boreholes have drawdown data for determining specific capacity.

- The 16 holes have an average depth of 50 metres

- The mean yield is 5.8 m3/hr.

- The tested discharge rate ranges from 0 to 14.4 m3/hr. The wide range in tested yields is caused by differences in lithological and structural site conditions, especially the rock type and presence of fractures/fissures

- Two aquifers were encountered at an average of 14, and 30 - 42 metres

- Static water level averaged 5.5 metres.

Hydrogeological and geophysical investigations were then carried out in the area. Briefly, the findings of the investigations are as follows:

Geology

The area is underlain by the rocks of Kavirondo and Nyanzian Systems. Most of the swampy areas are characterized by fine silty clays, of a maximum depth of one metre. These areas are underlain by laterites and/or ironstones that attain a maximum depth of 5 metres. In the area not covered by the swamps the laterites outcrops forming a capping zone. Underlying the laterites are highly decomposed metasediments mainly the grits, which grade downwards to the slightly weathered to marginally fractured grits. The area to the northeast is underlain by the dolerite dyke of the Amukura Hills. These dolerites intrude into the weathered metasediments (grits) causing the aquifer to wedge out. The Basement in this area is formed of massive and compact grits and/or mudstones in some locations.

Hydrogeology

The rocks of the Kavirondo System underlying the site are recharged directly by the rainwater. There is also little runoff that provides copious amounts of water for groundwater recharge after evaporation. The drainage also constitutes a marshy perennial streams that flow southwards into the River Sio that trends south-westwards into Lake Victoria. The marshy streams enable yet another mode of lateral recharge.

The summary of the Nambale Centre aquifer is as follows:

The groundwater potential of the Nambale Centre Aquifer is quite high:

- The groundwater potential increases steadily in the southwest direction from the Nambale Centre close to the water supply towards Nasira and Busibwabo area.  In the northwest direction the aquifers tapers and disappears at the Tangakona Centre due to impervious diorites of Amukura Hills to the northeast. Similarly the aquifer tapers and wedges out at the Nambale Urban Primary School just after the Nambale River due to Kisoko hills.

- 8 boreholes drilled into this aquifer have their drawdown data above 0.5 m3/hr/m except for the C 8354, which was drilled at the northwest fridges of the aquifer.

- Borehole for the ACK Church recorded no drawdown despite testing for 24 hours. The discharge of 14.4m3/hr denotes the pump capacity rather than the aquifer potential.

- The specific capacity for the 7 averaged 1.068m3/hr/m. Therefore with static water level at 5 metres and the borehole depth at 50 metres. There exists a 25 metre water column available for abstraction leaving 15 metres water column above the pump level to be installed at 45 metres. This gives potential of about 26.7 m3/hr per borehole (specific capacity of 1.068 m3/hr/m for 25 metres), which translates to 534 m3/day assuming a 20 hour pumping regime.

Geophysical Results

The results of the geophysical sounding are as shown in Table 10.5:

Table 10.5 Results of Geophysical Sounding

| VES Number | Location | Aquifer thickness (m) | Resistivity (Ohm.m) | Remarks |
| --- | --- | --- | --- | --- |
| VES 1 | Brigadier Sifuna Farm | 25 | 48 | Outside the Nambale aquifer |
| VES 2 | Nambale Urban Pri. Sch. | None |  | Dry Borehole: Eastern boundary of the aquifer |
| VES 3 | Nambale Sec. | 22 | 34 |  |
| VES 4 | ACK Church | 20 | 33 |  |
| VES 5 | Nambale Hosp. | 28 | 30 |  |
| VES 6 | Nambale water supply | 33 | 85 |  |
| VES 7 | C7540 – Oguto | 29 | 45 |  |
| VES 8 | St. Mary DEB Pri. Sch. | 4.5 | 42 | Northeastern boundary |
| VES 9 | Tangakona C 7539 | 6 | 53 | Northeastern boundary |
| VES 10 | 1 km from Tangakona towards Busibwabo | 10 | 27 | Northern boundary |
| VES 11 | Onyunyuri Village | 15 | 8 | Northwestern boundary |
| VES 12 | Nasira Pri. Sch. | 40 | 58 |  |
| VES 13 | Alungoli Centre | 10 | 30 |  |
| VES 14 | Useful and ornamental tree nursery | 54 | 44 |  |

The results of the geophysical sounding indicate that the Nambale Centre Aquifer tapers to the east at the Nambale Urban Primary along the Nambale River, and northeastwards at Tangakona and St. Mary’s DEB Primary School. The Onyunyuri Village marks the northern boundary of the aquifer. The aquifer thickens in the southeast direction towards Busibwabo with resistivity reflecting increasingly coarser material.

The location of boreholes in which geophysical sounding was carried out is given in Figure 10.6 on Page 10 -16.

- Proposed Scheme for Nambale Water Supply from Boreholes.

Based on the results of the groundwater potential evaluation study, it is proposed that groundwater be considered as a possible source for the expanded water supply to Nambale Town.

Under this Scheme, Nambale Town would be supplied from 4nr boreholes, each with an average yield of 500m3/d, giving the ultimate (year 2025) requirement of 1865m3/d. The water would be pumped to 2nr elevated storage reservoirs of capacity 500m3 each (total storage capacity 1,000m3). From the storage reservoirs the water would be gravitated into the Town’s distribution network after chlorination.

Briefly the proposed scheme comprises:

- 4nr boreholes, 50m deep, each with a yield of 500m3/d

- Pumping Mains from the boreholes to storage reservoirs – 150mm dia ferrous pipe mains, each approximately 500m long.

- 2nr Elevated Storage Reservoirs, capacity 500m3 each.

- Chlorination Arrangement at the storage reservoirs site, consisting of a ground level chlorine mixing tank and a pump to lift chlorine solution to the elevated storage tanks.

Table 10.6 outlines the estimated costs for Alternative Scheme 4.

Figure 10.6

Table 10.6 Estimated Costs for Alternative Scheme 4

| DESCRIPTION |  | UNIT | QTY | RATE | AMOUNT (Kshs) | AMOUNT (Euros) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Drilling and Equipping new boreholes, 2nr each 50m deep | nr | 2 | 1,500,000.00 | 3,000,000.00 | 34,090.91 |
| 2 | Manifold from boreholes to storage tanks - 150mm dia ferrous pipes | m | 2,000 | 5,070.00 | 10,140,000.00 | 115,227.27 |
| 3 | 2nr Elevated Storage Tanks - 500m3 | nr | 2 | 9,500,000.00 | 19,000,000.00 | 215,909.09 |
| 4 | Chlorination arrangement at elevated reservoirs site | L.S |  |  | 2,500,000.00 | 28,409.09 |
| 5 | Power supply connection to borehole site | nr | 4 | 1,000,000.00 | 4,000,000.00 | 45,454.55 |
| 6 | Distribution Mains |  |  |  |  |  |
|  | 50-200mm | m | 5,000 | 2,768.14 | 8,304,416.40 | 94,368.37 |
|  | 50-25mm | m | 5,000 | 874.16 | 1,748,318.92 | 19,867.26 |
| SUB TOTAL 1 |  |  |  |  | 48,692,735.33 | 553,326.54 |
| Add 20% of Sub-Total 1 for Preliminaries & General Items |  |  |  |  | 9,738,547.07 | 110,665.31 |
| SUB TOTAL 2 |  |  |  |  | 58,431,282.39 | 663,991.85 |
| Add 7.5% of Sub-Total 2 for Physical Contingencies |  |  |  |  | 4,382,346.18 | 49,799.39 |
| SUB TOTAL 3 |  |  |  |  | 62,813,628.57 | 713,791.23 |
| Add 9% of Sub-Total 3 for Consultancy Cost for Design, Tender Document Preparation and Supervision |  |  |  |  | 5,653,226.57 | 64,241.21 |
| GRAND TOTAL FOR ALTERNATIVE SCHEME 4 |  |  |  |  | 68,466,855.14 | 778,032.44 |

*1 Euro = 88 Kshs (Jan 2006)

## Economic Analysis of the Alternative Water Supply Schemes

In order to identify and select the most economical water supply scheme, an economic analysis has been carried out for the alternative schemes studied.  A discounted cash flow analysis has been carried out for each scheme over the 20 year project period up to year 2025. Details of the costs considered in the analysis are given below.

### Project Costs

- Capital Costs

Estimated capital costs of the alternative schemes are given in Tables 10.1 to 10.5. The costs are based on current market prices or derived from current on going projects such as the Nyeri Water Supply Project, Eldoret Sanitation Project etc.

- Maintenance Costs

The annual maintenance costs have been taken as 1% of the capital cost for permanent structures like intakes, pipelines, pumping stations, treatment works etc and as 5% of the capital cost for mechanical installations like pumps.

- Renewal Costs for Pumps and Motors

Pumps and motors require replacement at the end of their 10 year economic life. An annual allocation for their renewal cost has been considered in the analysis.

In gravity schemes the pump renewal costs considered are the costs of backwash pumps. In pumping schemes raw and treated water pumps make up the main element of pump renewal costs.

- Electricity Costs

Electricity costs have been estimated based on the current Kenya Power and Lighting Company (KPLC) Tariff of Kshs12 per kWh. In the pumping scheme the main electricity costs are costs of raw and treated water pumping. In the gravity schemes the electricity costs considered are the costs of backwash and domestic water pumping within the treatment works.

Details of the annual power requirements and costs are given in Appendix A.1.

- Chemical Costs

These include the costs of Alum and Chlorine. Details of annual chemical requirements and costs are given in Appendix A.2.

- Staff Costs

The staff costs are based on the proposed organisation structure given in Section 8 for the water service provider, the Western Water and Sanitation Service Company (WEWASSCO). These costs include costs for the Busia Area Office staff and the Corporate Team (Head Office).

The Head Office costs have been apportioned to the three schemes to be managed by WEWASSCO, i.e. Kakamega, Busia and Nambale, in the ratio of the projected year 2025 water demand in each scheme as follows:

| Municipality | Year 2025 Demand (m3/d) | Municipality’s Demand as % of Total |
| --- | --- | --- |
| Kakamega | 21,676 | 59.6 |
| Busia | 12,846 | 35.3 |
| Nambale | 1,865 | 5.1 |
| Total | 36,387 | 100 |

The percentage of WEWASCO Head Office Costs allocated to the Nambale Scheme is thus 5.1% of the total cost. Details of the staff costs are given in Appendix A.3.

- Indirect Costs

These include such costs as overhead costs for the water service provider, license fees payable to the Water Board and the Water Resources Management Authority, leave, health insurance, sick leave, gratuity etc. These are estimated to be 20% of the overall cost of a scheme.

### Discounted Cash Flow Analysis

Rates of 12%, 10% and 8% have been used to calculate the present day values of the scheme costs over a period of 20 years for the discounted cash flow analysis. These are detailed in Tables 10.7 to 10.11.

TABLE 10.7 Capital Costs of Alternative Schemes

| Component | Scheme 1 (Gravity Scheme from Malakisi River) | Scheme 2 (Pumping Scheme from Sio River) | Scheme 3 (Supply by pumping from Busia Treatment Works) | Scheme 4 (Supply from Boreholes) |
| --- | --- | --- | --- | --- |
| Civil Works (Kshs) | 301,050,146.81 | 112,789,135.22 | 210,341,348.03 | 59,473,885.64 |
| Pumps and Motors (Kshs) | 3,027,200.00 | 7,427,200.00 | 11,182,977.43 | 9,000,000.00 |
| Total Cost (Kshs) | 304,077,346.81 | 120,216,335.22 | 221,524,325.45 | 68,473,885.64 |
| Total Cost (Euro) | 3,455,424.40 | 1,366,094.72 | 2,517,321.88 | 778,112.34 |

TABLE 10.8 Annual Operation and Maintenance Costs for Alternative Schemes

| Component | Scheme 1 (Gravity Scheme from Malakisi River) | Scheme 2 (Pumping Scheme from Sio River) | Scheme 3 (Supply by pumping from Busia Treatment Works) | Scheme 4 (Supply from Boreholes) |
| --- | --- | --- | --- | --- |
| Maintenance Costs (Kshs) | 3,161,861.47 | 1,499,251.35 | 2,662,562.35 | 1,044,738.86 |
| Electricity Charges (Kshs) | 498,633.92 | 4,253,970.65 | 7,342,820.82 | 4,271,140.44 |
| Chemical Costs (Kshs) | 1,491,760.21 | 1,491,760.21 | 1,491,760.21 | 729,348.21 |
| Staff Costs (Kshs) | 9,483,050.45 | 10,722,818.45 | 10,722,818.45 | 10,722,818.45 |
| TOTAL COSTS (Kshs) | 14,635,306.06 | 17,967,800.67 | 22,219,961.84 | 16,768,045.96 |
| TOTAL COSTS (Euro) | 166,310.30 | 204,179.55 | 252,499.57 | 190,545.98 |

TABLE 10.9 Total Costs Over 20 Year Period – Present Value at 12% Discount Rate

|  | Component | Scheme 1 (Gravity Scheme from Malakisi River) (Kshs) | Scheme 2 (Pumping Scheme from Sio River) (Kshs) | Scheme 3 (Supply by pumping from Busia Treatment Works) (Kshs) | Scheme 4 (Supply from Boreholes) (Kshs) |
| --- | --- | --- | --- | --- | --- |
| A | Capital Cost | 304,077,346.81 | 120,216,335.22 | 221,524,325.45 | 68,473,885.64 |
| B | Recurrent Costs |  |  |  |  |
|  | Maintenance | 23,617,345.98 | 11,198,573.45 | 19,887,859.38 | 7,803,617.99 |
|  | Pumps & Motors Renewal after 10 yrs | 974,677.38 | 2,391,359.62 | 3,600,619.44 | 2,897,759.13 |
|  | Chemical Costs | 11,142,618.82 | 11,142,618.82 | 11,142,618.82 | 5,447,825.37 |
|  | Electricity Charges | 3,724,517.97 | 31,774,793.97 | 54,846,786.13 | 31,903,042.71 |
|  | Staff Costs | 70,833,110.76 | 80,093,487.94 | 80,093,487.94 | 80,093,487.94 |
|  | SUB TOTAL | 414,369,617.72 | 256,817,169.03 | 391,095,697.17 | 197,132,476.26 |
| C | Indirect Costs (20%) | 82,873,923.54 | 51,363,433.81 | 78,219,139.43 | 39,426,495.25 |
| TOTAL COSTS (Kshs) |  | 497,243,541.27 | 308,180,602.84 | 469,314,836.60 | 236,558,971.51 |
| TOTAL COSTS (Euro) |  | 5,650,494.79 | 3,502,052.30 | 5,333,123.14 | 2,688,170.13 |

TABLE 10.10 Total Costs Over 20 Year Period – Present Value at 10% Discount Rate

|  | Component | Scheme 1 (Gravity Scheme from Malakisi River) (Kshs) | Scheme 2 (Pumping Scheme from Sio River) (Kshs) | Scheme 3 (Supply by pumping from Busia Treatment Works) (Kshs) | Scheme 4 (Supply from Boreholes) (Kshs) |
| --- | --- | --- | --- | --- | --- |
| A | Capital Cost | 304,077,346.81 | 120,216,335.22 | 221,524,325.45 | 68,473,885.64 |
| B | Recurrent Costs |  |  |  |  |
|  | Maintenance | 26,918,709.08 | 12,763,971.92 | 22,667,894.24 | 8,894,450.82 |
|  | Pumps & Motors Renewal after 10 yrs | 1,059,952.95 | 2,600,582.24 | 3,915,641.50 | 3,151,287.19 |
|  | Chemical Costs | 12,700,195.64 | 12,700,195.64 | 12,700,195.64 | 6,209,352.50 |
|  | Electricity Charges | 4,245,151.67 | 36,216,450.22 | 62,513,572.90 | 36,362,626.27 |
|  | Staff Costs | 80,734,554.30 | 91,289,398.17 | 91,289,398.17 | 91,289,398.17 |
|  | SUB TOTAL | 429,735,910.45 | 275,786,933.40 | 414,611,027.90 | 214,893,858.06 |
| C | Indirect Costs (20%) | 85,947,182.09 | 55,157,386.68 | 82,922,205.58 | 42,978,771.61 |
| TOTAL COSTS (Kshs) |  | 515,683,092.54 | 330,944,320.08 | 497,533,233.48 | 257,872,629.67 |
| TOTAL COSTS (Euro) |  | 5,860,035.14 | 3,760,730.91 | 5,653,786.74 | 2,930,370.79 |

TABLE 10.11 Total Costs Over 20 Year Period – Present Value at 8% Discount Rate

|  | Component | Scheme 1 (Gravity Scheme from Malakisi River) (Kshs) | Scheme 2 (Pumping Scheme from Sio River) (Kshs) | Scheme 3 (Supply by pumping from Busia Treatment Works) (Kshs) | Scheme 4 (Supply from Boreholes) (Kshs) |
| --- | --- | --- | --- | --- | --- |
| A | Capital Cost | 304,077,346.81 | 120,216,335.22 | 221,524,325.45 | 68,473,885.64 |
| B | Recurrent Costs |  |  |  |  |
|  | Maintenance | 31,043,621.98 | 14,719,870.78 | 26,141,429.65 | 10,257,400.09 |
|  | Pumps & Motors Renewal after 10 yrs | 1,157,505.56 | 2,839,926.43 | 4,276,016.96 | 3,441,315.42 |
|  | Chemical Costs | 14,646,321.68 | 14,646,321.68 | 14,646,321.68 | 7,160,848.28 |
|  | Electricity Charges | 4,895,661.36 | 41,766,110.94 | 72,092,897.16 | 41,934,686.41 |
|  | Staff Costs | 93,105,987.23 | 105,278,212.21 | 105,278,212.21 | 105,278,212.21 |
|  | SUB TOTAL | 448,926,444.61 | 299,466,777.26 | 443,959,203.12 | 237,059,205.53 |
| C | Indirect Costs (20%) | 89,785,288.92 | 59,893,355.45 | 88,791,840.62 | 47,411,841.11 |
| TOTAL COSTS (Kshs) |  | 538,711,733.53 | 359,360,132.71 | 532,751,043.74 | 284,471,046.64 |
| TOTAL COSTS (Euro) |  | 6,121,724.24 | 4,083,637.87 | 6,053,989.13 | 3,232,625.53 |

### Conclusion

- The most economical scheme on the basis of initial capital investment is Alternative Scheme 4, Supply from Boreholes, at a capital cost of  Kshs 68,473,885.64 (Euro 778,112.34)

- The most economical scheme on the basis of 20 years Discounted Cash Flow Analysis for capital and maintenance costs is Alternative Scheme 4, Supply from Boreholes, at a Discounted 20 year total cost of  Kshs 236,558,971.51 (Euro 2,688,170.13)

### Recommendation

Alternative Scheme 4, Supply from Boreholes, works out to be the most economical both in terms of initial capital cost and 20 year Discounted Cash Flow Analysis for capital and maintenance costs

Therefore, it is recommended that Alternative Scheme 4, Supply from Boreholes, be adopted.

Briefly, the scheme would consist of the following components:

- 4nr boreholes, 50m deep, each with a yield of 500m3/d

- Pumping Mains from the boreholes to storage reservoirs – 150mm dia ferrous pipe mains, each approximately 500m long.

- 2nr Elevated Storage Reservoirs, capacity 500m3 each.

- Chlorination Arrangement at the storage reservoirs site, consisting of a ground level chlorine mixing tank and a pump to lift chlorine solution to the elevated storage tanks.

- 10km of Distribution Mains

The estimated total cost for the scheme would be as follows:

Initial Capital Cost			-	Kshs 68,473,885.64 (Euro 778,112.34)

Capital Cost per head			-	Kshs. 1,621.53 (Euro 18.43)

Annual Running Cost per head 	-	KShs. 397.08 (Euro 4.51)

# PROPOSAL FOR DEVELOPMENT OF A WATER BORNE SANITATION SYSTEM IN NAMBALE TOWN

## General

Nambale Town does not have a water borne sanitation system at present. Most households rely on on-plot sanitation facilities, predominantly pit latrines. Some institutions such as the hospital and government facilities have septic tanks.

With the expected growth in population and commercial activities in the Town and the proposed increase in water supply to the Town to 2000m3/d by year 2025, it is proposed to develop a water borne sanitation system.

A proposal for the expansion of the Sanitation System has been developed based on the Municipality’s topography, population growth, development trends and land use patterns.

## Sewerage Drainage Area

An analysis of the topography of the Nambale Area shows that the area slopes towards the Sio River, flowing approximately 2km south of the Town. A sewer system can be constructed to convey sewage by gravity to a Treatment Works to be located south west of the town near the Sio River.

## Estimation of Wastewater Generation

The land use plan for the Town has been used in the estimation of sewage volumes expected to be generated in the areas to be sewered.

The areas proposed to be sewered are the high development areas along the Mumias-Nambale-Busia Road, the Nambale-Amukura Road and the Nambale-Mundika Road. The consumers along these areas are mainly commercial and institutions.

The Land Use Plan for Nambale Town is shown in Figure 11.1 on page 11-2.

A layout plan showing the extent of the proposed sewage coverage area is given in Figure 11.2 on page 11-3.

Figure 11.1 Land use patterns in Nambale

Figure 11.2 Extent of Proposed Sewerage Coverage Area

Estimation of sewage flows has been based on water consumption and effluent production figures for different consumer groups given in the Water Design Manual (Ministry of Water and Irrigation), the World Health Organisation (WHO) Report No. 9 and results of recent water demand studies carried out for other urban municipalities in Kenya. The figures are given in Table 11.1 below:

Table 11.1 Sewage Generation Rates from Various Types of Water Consumers

| Type of Establishment | Daily Water Supply (l/c/day) | Daily Water consumption (l/c/day) | Unit | Sewage Reduction Factor [%] | Quantity of Sewage Flow (l/c/day) |
| --- | --- | --- | --- | --- | --- |
| Residential - High Income - Medium Income - Low Income | 120 90 60 | 90 67.5 45 | Head Head Head | 75 80 85 | 67.5 54 38.25 |
| Commercial Institutions | 20,000 l/Ha/day | 15,000 l/Ha/day | Ha | 85 | 12,750 l/Ha/day |
| Hospitals - High Class - Medium Class - Low Class | 400 200 100 | 300 150 75 | Bed Bed Bed | 80 80 80 | 240 120 60 |
| Hotels - High Class - Low Class - Others | 600 100 300 | 450 75 225 | Bed Bed Bed | 80 80 80 | 360 60 180 |
| Industrial | 25,000 l/Ha/day | 18,750 l/Ha/day | Ha | 80 | 15,000 l/Ha/day |

In the table above, the Daily Water Supply includes unaccounted for water (ufw) of 25% of total supply. The Daily Water Consumption is the Daily Water Supply minus unaccounted for water.

In the derivation of the sewage flows to the Treatment Works it is estimated that there will be a 100% sewer connections where sewerage facility is provided.

The ultimate (year 2025) expected sewage flow into the Treatment Works is approximately 600m3/d.

## Options for Wastewater Treatment

Selection of a suitable Sewage Treatment Process is dependent on the following factors:

- Initial capital costs

- Operation and maintenance costs

- Effluent quality required

- Sludge stability required

- Land requirements

- Level of labour requirements

- Stability of process to shock loading

- Degree of pathogen removal

- Flexibility for expansion

- Ease of land reclamation

- Mechanisation

- Simplicity of operation

Several treatment processes may be considered for sewage treatment. These include:

- Waste Stabilization Ponds

- Activated Sludge Process

- Extended Aeration (Oxidation Ditches)

- Aerated Lagoons

- Bio filtration

- Anaerobic Digestion

- Reed Beds

- Floating Aquatic Plant Systems

- Land Application

For Nambale Town, only systems which are widely used, simple to operate, have low operation and maintenance costs and have a proven performance in developing country situations have been considered. In view of these considerations, the most suitable treatment process for Nambale Town is Waste Stabilisation Ponds Systems.

Waste Stabilisation Ponds (WSPs) are large basins in which sewage is treated by entirely natural processes, with algae playing a major role in providing photosynthetic oxygen. Retention times are long (>20 days) which results in high pathogen removal but also in high land area requirements. No mechanical plant is necessary (unless pumping is required to lift the wastewater into the first pond in the series) and all the energy needed for treatment is provided by sunlight. Consequently they are extremely cheap to operate and maintain.

Advantages of WSPs include:

- Simplicity of operation

- Low operational costs with minimal energy requirements

- Low maintenance costs

- High degree of pathogen removal

- High degree of security of treatment due to long retention times

- Ability to accept widely fluctuating loads due to long retention times

- Effluent ideally suited to agricultural reuse with good fertiliser value

Disadvantages of WSPs include:

- Large land requirements (adequate land is available in the vicinity of the Town)

- If disposal to a water body is required, relatively high final effluent suspended solids and BOD (due to algae) may have a detrimental effect depending on the water body in question.

Although listed as a disadvantage, the presence of algae should the final effluent should not pose a significant problem because:

- High algae levels are usually related to overloaded conditions. The final effluent from a correctly loaded pond is relatively clear.

- The algae may be incorporated rapidly into the food chain of a receiving water body if a suitable consumer organism is present.

WSPs are now recognised as the most suitable form of wastewater treatment system for developing countries due to their simplicity of operation and low operation and maintenance costs. In addition, suitable land is available at reasonable in the vicinity of Nambale Town. WSPs are therefore recommended as the most suitable wastewater treatment option for the Town.

## On-Plot Sanitation and Hygiene Campaigns

The sanitation system for the unplanned informal areas will be pit latrines. These areas are predominantly low income, high population density with water supply from communal water kiosks.

In Nambale Town 49% of the population is categorized as low income (see section 5.4 of this report). 30% of the low income group are considered to be residing in informal settlements. It is proposed that a construction program to build approximately 100nr Ventilated Improved Pit Latrines be carried out under the rehabilitation works program. In addition, an artisan training program and hygiene campaign will be instituted to improve the general sanitation in these areas.

A criterion of 8 persons per latrine has been adopted. The overall requirement of pit latrines is estimated as follows:

| Year | Total Population | No. of People Requiring Pit Latrines | Number of Pit Latrines Required |
| --- | --- | --- | --- |
| 2009 | 29,000 | 4,200 | 525 |
| 2025 | 42,228 | 6,200 | 775 |

## Components of the Proposed Nambale Sewerage System

The proposed development of the Nambale Sewerage System will involve the following components:

- Sewage Treatment Works – 1nr Sewage Treatment Works, consisting of Waste Stabilisation Pond Systems, with the following components:

    - Inlet Works with screens and ultra-sonic flow measurement devices

    - Anaerobic Ponds

    - Primary and Secondary Facultative Ponds

    - Maturation Ponds

    - Outlet Works

The Treatment Works will be located South West of the Town, near the Sio River, to where wastewater from the service area can flow by gravity. It will have an ultimate (year 2025) Design Capacity of 600m3/d.

- Sewers – approximate total length 6km

## Cost of the Proposed Nambale Sewerage System

Estimated capital costs of the Sanitation System’s expansion measures are given in Table 11.2. The costs are based on current market prices or derived from on going projects such as the Nyeri Water Supply Project, Eldoret Sanitation Project etc.

Table 11.2 Estimated Costs for the Proposed Nambale Sanitation System

| DESCRIPTION |  | UNIT | QTY | RATE | AMOUNT (Kshs) | AMOUNT (Euros) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 600m3/d Treatment Works | m3 | 600 | 27,300.00 | 16,380,000.00 | 186,136.36 |
| 2 | Sewers | m | 4,000 | 5,076.00 | 20,304,000.00 | 230,727.27 |
| 3 | Plot Connections | L.S |  |  | 5,000,000.00 | 56,818.18 |
| 4 | On-Plot Sanitation and Hygiene campaigns | L.S |  |  | 5,000,000.00 | 56,818.18 |
| SUB TOTAL 1 |  |  |  |  | 46,684,000.00 | 530,500.00 |
| Add 20% of Sub-Total 1 for Preliminaries & General Items |  |  |  |  | 9,336,800.00 | 106,100.00 |
| SUB TOTAL 2 |  |  |  |  | 56,020,800.00 | 636,600.00 |
| Add 7.5% of Sub-Total 2 for Physical Contingencies |  |  |  |  | 4,201,560.00 | 47,745.00 |
| SUB TOTAL 3 |  |  |  |  | 60,222,360.00 | 684,345.00 |
| Add 9% of Sub-Total 3 for Consultancy Cost for Design, Tender Document Preparation and Supervision |  |  |  |  | 5,420,012.40 | 61,591.05 |
| GRAND TOTAL FOR PROPOSED NAMBALE SANITATION SYSTEM |  |  |  |  | 65,642,372.40 | 745,936.05 |

*1 Euro = 88 Kshs (Jan 2006)

# FINANCIAL ANALYSIS

## Introduction

The primary objective of this chapter is to analyse and present the financial impact of improved water and sewerage management in the town of Nambale. The overall concept has been described and presented in the early chapters of this report. It will therefore not be repeated here and technical aspects will be referred to hereafter only if essential for a better understanding of aspects examined in the financial analysis.

The approach followed is that of a Cost/Benefit Analysis emphasising financial criteria with regard to the continued operation of a rehabilitated and expanded water supply and sewerage and management system. Included in the present evaluation, some aspects will be discussed with regard to an appropriate future tariff structure.

The data applied and the information used in forming the conclusions presented in this report originate in most cases from the data collected by our team during the reconnaissance period in the project area. If other sources have been used they have been cited accordingly. The data used and all conclusions forwarded hereafter are therefore based on the latest available information with bearing on project activities and the region in which the project is located.

All information related to aspects discussed in the report compiled either in graphical or tabular form, extending each over more than half a page, has been presented in Appendix B1: Financial Analysis. The latter has been structured to give either general information (Appendix B.1) or to inform on financial evaluation of the base version in constant and current terms (Appendix B.2 and B.3 respectively). The same numbering of tables has been used in all cases in order to ease the comparison of identical topics evaluated under varying assumptions.

## Principles and Procedures

The methodology adopted for the financial analysis follows the Guidelines for Project Assessment (GPA) of international donor agencies, based on widely accepted techniques for the appraisal of natural resources development projects. They therefore provide a good basis for achieving the necessary degree of uniformity and comparability of results of the present analysis with similar projects of different regions.

As stipulated in former sections, the planning period covers 20 years, and the year 2006 has been chosen as the starting year of implementation. All benefits and costs have been valued in 2005 prices. Further general assumptions apply:

Monetary unit: mill. Euro (€)

Base year of cost estimates:  2005

Planning horizon:  2006 - 2025 (20 years)

Exchange rates:  2005  1€ = KSh 88.00

All calculations are done in Euro. The rates applied to update future costs and benefits to current prices as well as exchange rates used to convert local currency into Euro are those shown in the Table 12.1 following below.

Table 12.1: Exchange Rates and Inflation Factors

|  | 2005 | 2010 | 2015 | 2020 |
| --- | --- | --- | --- | --- |
| Exchange rate 1) |  |  |  |  |
| - Euro | 88,0 | 107 | 119 | 122 |
| Inflation Factor |  |  |  |  |
| - Foreign | 2,5 | 1,5 | 1,5 | 0 |
| - Local | 8,0 | 5,0 | 3,0 | 0 |

Source: various statistical yearbooks, inflation rates have been assumed by the Consultant

1) Kenya Shilling (KSh) per unit of foreign exchange

Above inflation rates are assumed to apply throughout the planning period. Local rates, in particular, may appear to be rather optimistic, yet, they are believed justified as they may reflect the currently rather favourable economic development in Kenya. As from year 2020 onwards, no further inflation has been taken into account as any development beyond that date is considered to be too speculative.

The opportunity cost of capital (discount rate) has been assumed to be 12 %, considered by many donor agencies to be the appropriate rate with regard to the financial evaluation of projects providing basic needs in Kenya such as water supply and sewerage services. However, alternative rates have been applied where sensitivity factors ask for a widened judgement, particularly with regard to the determination of dynamic unit costs.

Cost of facilities and equipment, which already exist at  the start-up of the rehabilitation  and expansion works with regard to both water supply and sewerage, where applicable, have been regarded as sunk costs and have consequently not been taken account of with regard to financing and depreciation. Values of existing assets, however, have been determined in order to calculate maintenance costs to be taken account of in ongoing as well as future operations. Residual values for rehabilitated and new assets with an economic life beyond the planning period have been considered, even though their value, because of discounting practices, becomes negligible. For assets, such as mechanical and electrical equipment, whose economic service life ends within the planning period, future replacement costs have been included.

Value added tax (VAT) has not been included in the analysis, except for production factors such as energy and chemicals, which have been majored at a rate of 16%. According to the specific organisational set-up of the recommended project, by which the overall management will be mainly the responsibility of the public Head Organisation, the Western Water and Sanitation Service Company in combination with the Municipality, there services will be exempted from VAT payments. This may be justified, as extra VAT charges may easily raise water fees above levels the majority of the population will neither be able to afford nor willing to pay, which would put the potential success of the project at stake from the beginning.

Accordingly, other taxes and duties, such as excise tax and import duties, have also not been taken account of, as those charges, according to our information, do not apply in Kenya when projects of national interest, such as water and sanitation management, are concerned. However, profits generated by the Water Service Provider have been subjected to taxes at a rate of 30% of the Net Income before tax (see Table 8: Cash Flow, Table 9: Income & Expenditure Statement and Table 10: Sources & Application of Funds, attached to the present for verification in Annex B2 and Annex B3 in constant and current terms respectively) .

Secondary benefits and costs not quantifiable in monetary terms, have not been taken account of here.

Price increases will be taken account of as composite annual rates of foreign and local inflation. The corresponding ratio of each category will depend on the amount of local and foreign investment costs, including physical contingencies but excluding costs for Detailed Design and Supervision.

The analysis is based on the assumption that the future water supply and sanitation will finally be operated under the cover of the Western Water and Sanitation Service Company with operational responsibility for day to day operations granted to the municipality. However, to achieve a high standard of managerial efficiency, particularly with regard to fee collection and to ensure enforcement of necessary regulations with regard to water supply and sewage services in general terms, a close co-operation between the head organisation and the municipality involved in the water supply and waste water disposal activities, will be essential.

The present financial analysis is comprised of the following two components:

- profitability analysis, and

- cash flow (financial statement) analysis.

The profitability analysis relies on discounting methods of the cash flow induced by the implementation and operation of the proposed water supply and sewerage system, including financing, operation and replacement costs. They are compared to the revenues generated by the entity once in operation. The main elements are the:

- dynamic unit costs (prime costs) of water supply, and the

- financial internal rate of return (FIRR)

The cash flow analysis, on the other hand, is based on accounting principles. It serves to determine the liquidity and overall financial status of the enterprise. The impact of the financing conditions assumed is incorporated in the cash flow analysis.

The economic viability, finally, of the recommended water supply and sewerage concept has been judged on the basis of three decision criteria, as follows:

- the Internal Rate of Return (IRR),

- the  Net Present Value (NPV), and

- the Benefit-Cost Ratio.

Each of the above criterion on its own may not suffice to comprehensively judge the outcome of the assessment. In combination, however, with the financial tables such as the Cash flow, Income and Expenditure Statement and the Sources and Application of Funds, they form an appropriate basis for final judgement.

## Project Costs

All costs presented hereafter are estimates. They correspond to actual conditions with regard to civil works and all locally to be procured equipment and materials and are based on our experience in the planning of corresponding projects under conditions similar to those in Kenya. Costs for internationally to be procured mechanical and electrical equipment and material are based on information collected in the region. They refer to state of the art technologies appropriate for the conditions in the project area and least cost solutions in particular with regard to efficient water supply and sewerage operations.

A more detailed discussion of project costs as appropriate for financial analysis follows in chapters 1.3.1: Investment Costs, and 1.3.2: Operation and Maintenance Costs below.

### Investment Costs

Investment costs have been determined by the structural and operational requirements necessary to achieve the given objectives. Structural requirements, design criteria and technical designs as well as cost estimates have been explained in detail in Chapters ? and ?  further up in this report. All costs with regard to the recommended concept have been identified in sufficient detail so as not to invalidate final conclusions and recommendations given in the present report.

It should be noted that the implementation schedule clearly distinguishes between two distinct phases. They are recapitulated as follows:

- Rehabilitation works: 	assumed to be realised between 2006 and 2007, and the

- Expansion works	which have been scheduled to be implemented between

2007 and 2009 as well as in 2015 in order to optimise

the allocation of scarce financial resources.

As can be seen from above timing, it has been assumed that part of the rehabilitation and the expansion works can be executed in parallel so as to assure the achievement of full operational conditions as early as possible.

Detailed investment cost estimates are given in Appendix A.1. They are shown in aggregate form in Tables 6 to 7, based on 2005 prices. Table 5 informs on the value of existing assets. Table 6 refers to major rehabilitation works necessary to bring the system back to about the original design capacity while Table 7 covers the investment costs with regard to the expansion of the water supply and sanitation system envisaged. A global implementation schedule is presented in Table 1.1: Implementation Schedule, which shows the successive completion of all implementation stages in percentage rates. All information mentioned has been presented in Appendix A.1: Basic Information.

Table 1.1: Investment Schedule translates the time schedule into an investment schedule (see Table 1.2), informing on combined rehabilitation and expansion investments and their distribution during the planning period. The table distinguishes between constant (see Appendix A.2) and current terms, presented in Appendix A.3 respectively.

Costs distinguish between local and foreign portions of investment costs according to the origin of the equipment and material, including indirect foreign exchange costs. The proportions of local and foreign cost components of the Nambale scheme are 65 % and 35 % respectively. In estimating the import content of the local investment cost component of the present project, data (adapted according to our estimates) of a former study on water management in a country similar to Kenya has been used to determine the import requirements of locally produced goods and services.

All unit costs are assumed to comprise freight and installation (where applicable). In order to account for uncertainties in planning, a physical contingency of 7.5 %, excluding costs for land, and a financial contingency according to the periodical inflation rates cited in Table 1 above have been included. Costs for Detailed Design and tendering as well as for consultancy services have been included at a rate of 9%.

Table 2 below recapitulates investment costs by distinguishing between major components together forming the recommended water management concept, in constant 2005 prices both in Euro and Kenyan Shillings (KSh).

Table 2:  Overall Investment Costs in 2005 prices

Depreciation, calculated on a straight-line basis, is considered according to the economic life of all components of civil works, equipment and vehicles. The individual duration of their corresponding service life has been estimated based on the values given in the Design Manual for Water Supply in Kenya from the Ministry of Water and Irrigation as shown hereafter. Land is not depreciated.

- Civil works, dams, boreholes	40 years

- Pumps, Diesel engines	10 years

- Electric motors, switch gear	10 years

- Mechanical equipment		10 years

- Mobile equipment		  7 years

Replacement and depreciation costs and their development in the course of the planning period have been computed and presented in Table 2: Replacement and Table 9: Income and Expenditure Statement, both in constant and current terms, see Appendices A.2: Financial Analysis in constant and Appendix A.3: Financial Analysis in current terms, respectively.

Based on the service life mentioned above and the corresponding period of active service of each item by the end of the planning period, salvage values have been computed as shown below and have been included (as negative investments in the year 2025) in the analysis.

Table 3:   Salvage values

| ###### Component | Salvage values, mill € (in constant 2005 prices) |  |  |
| --- | --- | --- | --- |
|  | Civil works | Mechanical & Electrical equipment | Mobile equipment |
| Rehabilitation works | 0.1 | 0.1 | 0 |
| Expansion works | 0.5 | 0.2 | 0 |

### Operation and Maintenance (O&M) Costs

Recurrent costs refer to annual expenses required to continuously operate the water supply and sewage system. They include maintenance and operation expenditures such as energy, chemicals, personnel costs, including fringe benefits, and materials. They do not include regular cash outlays such as debt service charges and depreciation, as those have been computed separately. However, they include estimates on water extraction charges which will most likely be levied by the Government in the very near future.

Recurrent costs have been given special attention as the improved and expanded water management system in the project area must be looked at as a long term development which will, most likely, need financial support from outside, particularly during the initial years. Details as to the calculatory basis of operation and maintenance costs will be provided further down in this chapter.

The following four main groups have been taken into account as recurrent costs:

- Operation & Maintenance (O&M),

- Inputs,

- Personnel,

- Administration.

Operation & Maintenance (O&M),

In cases, where distinct unit rates, such as prices for fuel, energy, numbers of staff, etc. are not applicable, percentage rates as of the initial investments have been used to determine in particular maintenance costs. The rates applied in the present analysis originate from the Design Manual for Water Supply in Kenya from the Ministry of Water and Irrigation as well as on experience in similar projects. Those rates are as shown below. They do not include costs for personnel or financial costs such as interest and depreciation.

- Civil works			1.0 %

- M&E equipment 		  	3.0 %

- Mobile equipment 		  	5.0 %

It is worthwhile to mention that O&M costs have been calculated to increase gradually in such way that they will be below average values in the first half of the planning period and above average thereafter, to take account of higher costs of ageing equipment and material.

Inputs

In the present case, items under this heading can be limited to costs necessary for energy and chemicals only as other production factors generally summarised under ”goods and services” are not required.

The demand for electric energy has been based on the specific requirements of all water and sewage treatment plants and individual types of pump stations. The specific cost per KWh has been given as 0.12 €.

Costs for chemicals have not been taken into account for Nambale as the municipality does presently not own a sewerage system. Even though a corresponding plant will be introduced during the expansion programme, costs have been neglected in the present analysis as it is assumed that corresponding tasks will be covered by the existing staff.

Table 12.4: Chemical Rates and Prices

| Chemical | Kg/mill m3 | €/Kg | €/mill m3 |
| --- | --- | --- | --- |
| Alum | 30.000 | 0,34 | 10,283 |
| Soda ash | 0 | 0,13 | 0 |
| Chlor | 0 | 1,45 | 0 |
| Total |  |  | 10,283 |

Above cited quantities and prices correspond to about actual values which may in the future be applied in the Nambale water treatment plant. Unit prices include VAT at a rate of 16%.

Personnel

Technical staff required to supervise and to operate the entire system has been based on a ratio of total staff per connection (water supply only). Based on the relevant data for 2005 this ratio has been computed to be about 8 personnel units per connection in the year 2005 decreasing to 6 in 2010 and 4 in the year 2025.

The average wage rate per ”personnel unit” has been calculated to be 3,400 and 3,390 (rounded) € per person and year, including social charges and premiums paid by the operator for personnel for water supply and sewerage services respectively. The corresponding calculation is based on data specified in Table 12.5 below.

The number of staff corresponds to the planned organisation structure starting once the new management system will be in place, expected to come about in the very near future. It will include all staff of both the Technical and the Commercial Division.

Table 12.5:     Staff requirements   (2005 prices)

|  |  | Water supply | Sewerage |  |
| --- | --- | --- | --- | --- |
| Qualification | Wage/month | No of staff | No of staff | €/month 1) |
| Area Manager | 795 | 2 | 0 | 1,591 |
| Officer in charge | 558 | 3 | 0 | 1,675 |
| Supervisor | 341 | 4 | 0 | 1,364 |
| Administrative staff | 227 | 14 | 0 | 3,181 |
| Skilled worker | 196 | 2 | 0 | 391 |
| Unskilled w. | 165 | 3 | 0 | 494 |
| Total /Average |  | 28 | 0 | 3,727 |

1) including social charges

Water Extraction Fees

It is assumed that water fees will be levied by the Government with regard to water extraction from public sources in the very near future. To take account of this development corresponding costs at a rate of 10% of revenues based on the volumes water billed have been included in the present analysis.

Training

Given the fact that either water supply or modern sewerage techniques do not represent technologies not yet known to Nambale, training on a large scale to assure continuous and effective management and operation of the newly installed assets may not be required.

However, it is assumed that some training efforts will have to be directed towards the operation of the improved and enlarged system in order to achieve the envisaged objectives of more reliable and regular services to the optimum.

Realizing that concrete training programs may only be established in detail at the beginning of expanded operation, a lump sum of 50,000 € has been retained in our analysis, spent in two applications of 25,000 € each between the years 2007 and 2008. It is expected that important parts of the training program may be realized in co-operation with local agencies or projects operating in the area, benefiting from their previous experience in existing systems.

Administration

Administration costs include such cost items as staff (i.e. billing and customer relation services), office costs, insurance, equipment and materials. For staff, equipment and material, again a percentage rate has been applied. A rate of 20% for administration expenses covering staff, equipment and material assumed to be required to strengthen the work of the technical staff in the supervision and operation of the water supply and sewerage system has been calculated from the costs for staff presently employed. This is assumed to about correspond to actual conditions at present.

In addition, extra administration expenses have been taken into account as in the near future substantial managerial and supervisory tasks will be organized jointly through the Western Water and Sanitation Service Company Ltd. covering the four towns of Kakamega, Busia, Nambale and Mumias. The repartition of the corresponding total costs of € 191,000 per year (about 16,8 million KSh) has been done on the pro rata production of raw water per year and utility. Accordingly, Nambale has to bear about 3% of the costs, translating into € 6,000 per year.

Non operational expenses such as local bank interest, commission expenses and currency exchange losses have not been taken into account.

Total annual operation and maintenance costs throughout the planning period are summarised in Table 3: Operation and Maintenance referring to constant and current prices in Appendix B.2 and B.3 respectively.

For the benefit of an easy evaluation, total operation and maintenance costs with regard to the recommended water supply and sewerage system disposal concept, have been determined separately for each criteria as summarised in the table below.

Table 12.6: Average O&M costs per major components (constant prices)

| Cost factor | Unit | 2010 | 2015 | 2020 | 2025 |
| --- | --- | --- | --- | --- | --- |
| Maintenance | Mill. € | 0.03 | 0.04 | 0.04 | 0.05 |
| Energy | Mill. € | 0.02 | 0.04 | 0.05 | 0.06 |
| Chemicals | Mill. € | 0.0 | 0.0 | 0.01 | 0.01 |
| Personnel | Mill. € | 0.07 | 0.06 | 0.06 | 0.06 |
| Water Extraction Fees | Mill. € | 0.01 | 0.03 | 0.07 | 0.13 |
| Administration | Mill. € | 0.02 | 0.02 | 0.02 | 0.02 |
| Total | Mill. € | 0.15 | 0.19 | 0.24 | 0.32 |

The table refers to aggregate units based on the specification provided in the chapters cited above, while Table 3: Operation and Maintenance in Appendices B.2 and B.3, in constant and current terms, respectively, inform on main cost factors, such as maintenance, operation, staff expenditures and administrative costs, applying to all operational aspects listed in the table above. In addition, the table also informs on details as to the development of O&M costs over time throughout the project planning period. It may be examined both, in constant as well as current terms in the tables attached to the present as indicated above.

### Working Capital

In addition to the investment costs, provisions for working capital have been considered in order to ensure continuous operation of all activities, especially during the initial years of the project. The working capital has been estimated on the basis of minimum coverage required for different categories. The following has been assumed:

Operating cash:	1.0 month (= 8 %) of annual personnel costs,

Accounts receivable :	1.0 month (= 8%) of annual inflow

Inventories:	2.0 month (= 17 %) of maintenance costs

Increase in net working capital (N.W.C.), which is the balance between current assets and current liabilities, has been estimated by introducing a (calculatory) factor for accounts payable (approximately two months from annual personnel costs). For details see Table 4: Working Capital, Appendices B.2 and B.3, in constant and current terms respectively.

Increase in NWC may be used as an important indicator with regard to the liquidity of the organisation in charge. It is further considered in the calculation of the Cash Flow (see Table 8) and the Sources and Application of Funds Statement (see Table 10). Both tables may be reviewed in detail in Appendices B.2 and B.3, in constant and current terms respectively.

## Benefits

The provision of reliable water supply and sewage disposal services carries substantial benefits to households and enterprises alike. Households themselves value convenient and reliable supplies because of time savings, amenity and health benefits, in addition to cost savings, in particular for enterprises.

Details as to the organisational set-up of the newly to be established Water and Sanitation Service Company, and in particular relevant fee setting principles remain to be agreed upon. With regard to the evaluation of the financial viability the water supply and sewerage system will be regarded as one operational unit per town. Special conditions as to the operational relationship between the public Head Organisation and the operator in Nambale have thus not been taken into account. It is assumed that operational settings, particularly with regard to the power and responsibility each of the two parties concerned, including rules for the enforcement of regulations and the collection of the fees, will be agreed upon in the very near future.

With regard to revenue generation, it has been assumed that the operator, in principal, can rely on and freely dispose of the full amount of the water charges and waste water disposal fees from all consumers, including public and private enterprises taking part in the improved and expanded water supply and sanitation system.

### Water Charges

Revenues in the ideal case should permit to fully recover both, recurrent costs and capital expenditures of services provided. Experience, however, indicates that water supply and sanitation systems in low or middle-income countries are generally not self-supporting.

Indeed, the initial financial analysis for the present undertaking, based on the tariff structure in force at present, clearly proved that financial viability and economic sustainability of the services concerned can not be achieved. This does not come as a real surprise as the present tariff, even though it comprises all items, which in total regulate the service conditions with regard to water supply and sanitation, dates back to 1999 with neither increases nor corrections for inflation. Given for instance the inflation in Kenya of about on average 9% annually from 1999 to present, historical rates of 1999 would now be worth 1.82 times the original value, not counting real tariff increases.

It is meanwhile common understanding that services like most of all water supply to private, especially urban consumers are to be considered as basic needs. At the same time it is also generally accepted that the costs of such supplies should be borne by the users themselves. When this is the case, especially private households should have the opportunity to participate in the planning process with regard to the type of service they want. For large urban areas, however, where the long term provision of reliable supplies of the required quality is at stake, formal services are the norm. Private preferences as to the type of services become of subordinate emphasis while technical solutions orientated on the need for an optimal long-term water resources management gain priority.

Against this background it becomes obvious that more often complex water supply systems are required which are characterised by long construction periods on the one hand and only a gradual increase in the revenue extracted from the operation on the other. Cost recovery rather than profit maximisation becomes the main concern for the utility in charge of corresponding services. Relevant institutional arrangements include appropriate economic instruments to encourage especially non-domestic users to use the required services to the full. While this, most of all in a prosperous urban area may not pose a major problem, the corresponding situation for domestic users, especially in areas of more rural character such as Nambale, may be less obvious.

### Tariff Structure

Following the “full cost recovery principle”, our approach to revenue generation in the context of the present analysis, capable to meet the above mentioned challenge, is based on the tariff structure outlined in Table 4: Tariff Structure, presented in Appendix B.1: Basic Information, for closer examination.  The tariff structure outlined corresponds to the regulations in force in Kenya at present, however, the table referred to also informs on tariff developments over time in real terms.

The tariff structure in force at present, in order to achieve utmost charging equability, already combines financial with social elements, such as cross-over subsidisation. Groups with a higher financing capacity such as high income groups, public and private institutions, commercial and industrial enterprises consequently pay higher rates as less well off brackets of the population. Yet, the introduction of a tariff structure permitting financially viable and sustainable operations has taken priority. This includes that water will have to be paid for in full, even by consumers below 10 m3, who, according to present regulations, only pay a flat rate of 200 KSh per month. In addition, price increases of on average 12.25% per year have been assumed throughout the planning period. Details as to the principles followed are outlined hereafter.

In view to evaluate the financing capacity of domestic users of public services like water supply, information on financial resources at the disposal of different groups of the population concerned becomes the decisive criteria. The information available on household income applicable to the city of Nambale is vague and most likely not very reliable. Corresponding data give figures of about:

- 10,000 KSh per month for low income groups,

- 17,500 KSh per month for middle income groups, and

- 25,000 KSh for households with high income

The disposable household income may now be applied as a yardstick to determine the affordability of domestic consumers. By international standards it is commonly agreed that about 5 % of the disposable income represent an acceptable portion affordable by domestic consumers to pay for water supply and sanitation.

The order of magnitude of households belonging to different income categories based on percentage rates obtained in the region was given with 49, 40 and 11 % for low, medium and high income groups respectively.

Knowledge of the financing capacity of domestic consumers to pay for above services is a valuable information on its own but not yet sufficient to allow a judgement on the affordability. Additional information is required as to the water consumption per income group and the corresponding tariff structure to quantify monthly consumption bills in monetary terms.

Table 12.7: Household Water consumption per income group and monthly water bills

| Income group | Water consumption |  | Monthly bill |  | Affordable |
| --- | --- | --- | --- | --- | --- |
|  | l/c/d | m3/month | KSh/month | % | Income, KSh/month |
| Low | 60 | 9.9 | 250 | 2.5 | 500 |
| Medium low | 90 | 15.1 | 476 | 2.7 | 875 |
| High | 120 | 20.2 | 762 | 3.1 | 1,250 |

The monthly bill as been calculated according to the tariff structure assumed to be in force in 2008 to reflect more realistically the conditions for private households, as shown below. It does not include meter rent of on average 50 KSh (0.57 €) per connection (private households) levied on a monthly basis.

1  -  10 m3		25   KSh/m3

11  -  20 m3		32   KSh/m3, and

>     20 m3		38   KSh/m3.

Affordable income in above table refers to the capacity to pay for water supply and sanitation charges per income group based on 5 % of the disposable income including services related to sanitation. For the latter a ratio of about 50% of water charges has been applied.

Above figures, especially the monthly bill in percent of affordable income, show that the disposable income of domestic consumers would currently suffice on average to pay for water supply according to specific consumption and rates set by the tariff structure, as assumed for the present analysis.

However, it should be realised that affordability is an outside judgement, based on official information on the financing capacities of different consumer groups. It gives only very limited information with regard to their willingness to pay for the services offered.

If, for instance, in the course of new or extended water supply services water quality, as perceived by potential beneficiaries, will increase in future, due to the implementation of the proposed new scheme, or the supply of water will be more regularly and more efficiently as in the past, consumers’ willingness to pay will be positively affected. Consequently, if in the view of the community, felt needs are properly addressed by the improved and enlarged system, consumers are likely to contribute to those services even above the rates representing affordability. Affordability rates may thus be regarded as the lowest level of private resources available for the payment of public services.

Detailed investigations into affordability and willingness to pay, however, have not been included in the evaluation of cost recovery as it is extremely time consuming and demands very detailed information of socio-economic conditions of the population concerned, which was not available.

### Revenues

From Table 7: Revenues, presented in constant and current terms in Appendixes B.2 and B.3 respectively, it can be seen that the major portion of the operation revenues come from water sales and waste water charges. Whereby waste water charges have assumed to correspond to about 50 % of water charges in all consumer groups. The population connected to the sewerage system has been estimated to develop from 15% in 2010, increasing to 50% up to the year 2015 and remaining at that level thereafter, referring to families benefiting from piped water supplies.

Other major revenues originate from services rendered for water and sewerage connections. Non-operation revenues, such as interest received and other revenues such as late payment penalties and charges for closing and opening meters have not been taken into account.

According to the information provided, the average billing ratio, referring to the numbers of units billed (private households, enterprises etc.), does not correspond to figures commonly found in similar organisations. In our calculations we have assumed a rate of about 63% at present (2005), which will develop to 100% during the first five years (2010) of operation. On the other hand, the collecting ratio, defined as the percentage rate of payments out of the total amount billed, reaches 64 % at present. From there it may be concluded, that in the future corresponding inflows would hardly suffice to fully cover the service costs (recurrent costs and capital expenditures) of the new water supply and sanitation system once fully operational. For the benefit of realistic planning we have therefore assumed that the collection ratio would improve to 95% within the first five years of operation, where it will stay throughout the remaining planning period.

Managerial responsibility for pursuing activities required to achieve above improvements, such as public awareness campaigns to enhance consumers' willingness to pay, will be with both, the private operator as well as the public Head Organisation, including the enforcement and compliance with regulations.

### Other revenues

Other revenues may be generated by general services related to water supply programmes and in particular sanitation services, such as health education, service and maintenance contracts for large costumer. Corresponding income has been taken into account in the present analysis at a rate of 30% of waste water revenues.

Some revenues may also accrue from fines resulting from arrears payments. In line with financial management practices of similar organisations a rate in the range of one to five per cent of outstanding charges may apply. However, in the present case, corresponding revenues have not been considered.

A break-down of all revenues retained in the present analysis and their development over time is demonstrated in Table 7: Revenues, Appendices B.2 and B.3, in constant and current terms respectively. For the benefit of a closer examination, additional details have been provided in Table 1: Water Demand, in Appendix B.1, which informs on the present population, population coverage ratios, specific water demand and total water consumption as well as on total raw water volumes produced, including corresponding growth rates. Table 2: Water per User Group and Table 3: Connections, give further details as to specific water consumption per user group in million m3 per year and the number of connections per user group. In addition, Table 3 informs on assumed growth rates to determine the future number of non-household connections, while the development of household connections themselves has been linked to the development of population coverage. Increases have been assumed to develop according to the size of households, assumed to be 7.3, 6.0 and 5.0 members per household for the periods 2005 to 2009; 2010 to 2014 and 2015 to 2025 respectively.

## Project Financing

Detailed information as to the financing of the project could not be obtained in the project area. The financing pattern is therefore assumed to be as follows:

With regard to financing all investment costs, that is expenses for rehabilitation and expansion works have been taken into account, including, consultancy services. Total project costs come to € 2.19 million, equivalent to 192.7 million KSh (2005 constant prices).

Table 12.8: Financing

As proposed by the donor agency, financing conditions in the present case will follow the pattern of a mixed financing, often adopted for projects providing basic needs, combining a a soft loan component with a grant. Therefore we have planned the financing to be based on a soft loan which will cover about 80 % of total costs to be financed from external sources, while the remaining part of 20% will come as a grant from local sources (Government of Kenya). Equity financing by the Service provider is therefore not foreseen. Table 12.9 below summarises the information outlined above and informs on the disbursement schedule at the same time.

Table 12.9:  Financing pattern *)

| Loan | Unit |  | Disbursement |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Total | 2006 | 2007 | 2008 | 2009 |
| Soft loan | Mill € | 1.75 | 0.08 | 0.59 | 0,54 | 0,54 |
| Local loan | Mill € |  |  |  |  |  |
| Grant | Mill € | 0.44 | 0.02 | 0.15 | 0.14 | 0.14 |

*) all figures rounded

Detailed financing conditions have been summarised below:

Soft loan

- Interest rate:			2,5 % per annum

- Interest during construction:	0,25  % per annum

- Commitment charges: 	0,25  % of the outstanding loan

- Total loan period:		40  years

- Grace period:	 		10  years

- Repayment period: 	30  years

More detailed information as to the financing schedule may be taken from Table 5: Financing and Table 6: Dept Service in Appendices B.2 and B.3, where Table 5 informs on the financing schedule with regard to each type of loan, while Table 6 summarises the debt service in general terms.

Common to most investments in new water supply and sanitation activities in combination with slow revenue generation built-up, appropriate financing arrangements become one of the crucial focus points. Indeed, this also applies to the financial viability of the project recommended in the present report, as can be taken from the financial statements such as the Cash flow, Income and Expenditure Statement and Application and Sources of Funds in constant and current terms, attached to the present in Appendix B.2 and B.3 respectively. More detailed financing concepts will have to be reviewed, emphasising in particular the need for external financial support during the early years of operation, as revealed by the financial statement mentioned above. Relevant guiding principles are outlined below.

Because of the benefits of an efficient and reliable water supply and sanitation system accruing mostly to private users, including, next to households, private entrepreneurs in industry, commerce and services, consumer’s willingness to pay may be positively effected. However, given the tight economic situation currently prevailing in the region and the limited financing capacities of mainly the private users, water charges may hardly be increased beyond the rates discussed above, particularly not in the early years of the project, even though the need for financial support then is most demanding. Nevertheless, increases in water charges, particularly for the commercial and industrial sector, still remain a viable option in combination with an appropriate tariff structure, based on variable user charges combined with elements such as the polluter pays principle, increasing block rates and cross-over subsidisation based on financing capacities.

From the above it becomes clear that the development of one generally applicable funding strategy will most likely not be possible. Different options will have to be investigated, taking account of effective combinations of managerial and operational criteria as may be appropriate for the future operator, as well as the legal environment (liabilities, pollution regulations) under which the facility will have to operate.

In addition to the financing assumed by us, as outlined above, possible sources of extra funding, in particular during the start-up period of the present water supply and sewerage system disposal project, the following may be of importance:

- Subsidies by the Government of Kenya and/or the participating municipalities through national and/or regional environmental promoting programs (if applicable) through specialised funds such as Environmental Protection Fund (or similar, if applicable),

- short-term working capital credit by domestic commercial banks (capital market),

- local private investors (equity oriented financing by industries, small and medium sized enterprises and commercial enterprises),

- grants, donations and/or credit on preferential conditions  by international donors in relation to activities such as water supply and sanitary services as well as conservation of the environment (IBRD, “World Bank”; EBRD, European Bank for Reconstruction and Development, EC Commission; EIB, European Investment Bank),

Financial co-operation, lending conditions and credit terms of any funding arrangement will vary according to type of project, the risks involved and the requirements demanded by the financing agency. This may most of all concern the social policy (priority of private activities over state activities), legal regulations (obligation to adopt economical, financial and budgetary policies) and morality aspects (public desire for environmental safety and ecological efficiency) prevailing in Kenya at the time of implementation.

## Financial Analysis

### Profitability Analysis

The evaluation of the profitability of the waste disposal concept as recommended by the present report is based for one on the dynamic unit costs (prime costs) and secondly on the financial internal rate of return (FIRR).

Dynamic unit costs:

Dynamic unit costs represent break even rates per m3 of water handled and thus indicate the threshold of profitability.

For the benefit of a more detailed assessment of break even rates with regard to the operation of the new water supply and sewerage system disposal system, dynamic unit costs, as outlined in Table 10 below, have been determined to cover either:

- total project costs, or

- operation & maintenance (O&M) costs only.

Distinction has been made as to the discount rate applied. Lower discount rates may be applied since water supply and sanitation services in the present case is seen as a public responsibility and as such oriented on cost recovery as opposed to profit maximization. As water supply and sanitation is being regarded as a basic need for the population, carrying in addition various direct and indirect benefits for the nation, lower rates of return may be acceptable to the national economy. A lower discount rate would therefore be justified. In our computations of dynamic unit costs, discount rates of 12% have been set as standard. The impact of varying discount rates has been tested, as illustrated in Table 12.10 following below.

Table 12.10: Dynamic unit costs

|  |  | Unit | Discount rate (%) |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 8 | 10 | 12 |
| Raw water | Total costs | €/m3 | 1.02 | 1.08 | 1.13 |
|  | O&M only | €/m3 | 0.46 | 0.47 | 0.48 |
| Water billed | Total costs | €/m3 | 1.42 | 1.52 | 1.62 |
|  | O&M only | €/m3 | 0.65 | 0.66 | 0.68 |

Since dynamic unit costs are generally calculated in constant terms without taxes and financing above rates refer to dynamic unit costs in constant terms (2005 prices).

Financial Internal Rate of Return (FIRR):

According to the standard of international financing institutions, the financial internal rate of return (FIRR) is determined without inflation, taxes and depreciation (for informative purposes, the FIRR based on current terms has been added). Replacement costs and salvage values, however, are taken into account. No provision is made for financing conditions, when loan financing is considered.

In the case of public utilities, where the prices and consequently the revenues, are not determined by the market, but set instead by political decisions, the FIRR becomes less convincing as a profitability indicator. Because future revenues are fixed administratively, the FIRR does not allow much more information as compared to the dynamic unit cost. In fact, the FIRR may be considered as reflecting the results computed in the Specific Costs Analysis from a different angle. While the specific costs (dynamic unit costs) determine the threshold of profitability under the assumption of a given discount rate by specifying the break-even price of water, the FIRR takes the price of those fees as given and determines the corresponding break-even discount rate.

The calculation of the FIRR in the present case is based on revenue generation including tariff increases in real terms as discussed in Chapter 1.4.2 above. Our computations yield results as may be taken from Table 12.11 below. For details see Table 14 in Appendix B2 and B3

Table 12.11: Profitability

| Constant terms | Discount Rate |  |  | FIRR % |
| --- | --- | --- | --- | --- |
|  | 12% | 10% | 8% |  |
| Net Present Value (million €) | -0.41 | -0.04 | 0.51 | 9.8 |
| Benefit/Cost Ratio | 0.87 | 0.99 | 1.12 |  |
| Current terms |  |  |  |  |
| Net Present Value (million €) | -0.79 | pLE .43 | 0.11 | 8,4 |
| Benefit/Cost Ratio | 0.81 | 0.91 | 1.02 |  |

The use of the FIRR alone in evaluating the outcome of a project may suffice only if the FIRR arrived at happens to approximate the opportunity costs of capital (discount rate) in Kenya, which, in spite of social considerations with regard to tariff setting, must be considered to be close to 12%. Otherwise, the relative weighting given to timing of benefits and costs in the economic comparison is incorrect. Evaluation in the present case is therefore based additionally on parameters, which provide present values, so that a discount rate equivalent to the opportunity cost of capital can be applied. One alternative criterion has been provided, being the cost-benefit ratio.

The total NPV has the disadvantage that it does not give any indication of the relative productivity or efficiency of the investment in terms of the utilisation of the critical resource, capital. The B/C ratio alone may also not be wholly suitable for assessing the outcome of a project as it may be altered according to whether an item is put in the cost stream or the benefit stream. In combination, however, the profitability criteria retained will suffice to allow final judgement with regard to the outcome of the project.

### Cash Flow Analysis

Criteria to be tested will primarily be the cash flow. Additional financial tables, such as the  Income Statement and Expenditure as well as the Application and Sources of Funds have been included to allow comprehensive judgement. For the benefit of easy comparison, all relevant tables have been prepared in tabular form. All financial results are shown in both, constant (real) as well as current (nominal) terms, see Appendices B.2: Constant Terms and B.3: Current Terms, respectively. They will briefly be commented on below by quoting each time the table reference number and the corresponding appendix for closer examination.

The Income Statement and Expenditure (see Table 9 in Appendices B.2 and B.3), evaluates the operational performance of the entity as the balance between total revenues on the one side and operating costs, including O&M and depreciation, on the other. Operating Income less interest payments yields the Earnings before Tax (EbT). After considering tax payments, the Net Income (or loss) is obtained. Taxes on profits have been included at a rate of 30 % on EbT. However, in order to evaluate the outcome under the assumption that no taxes on income will be levied, the major financial tables, e.g. the Cash Flow (Table 11), the Income Statement and Expenditure (Table 12) and the Sources and Application of Funds (Table 13) have been presented in Appendices B2 and B3, excluding income tax.

The Sources and Application of Funds (see Table 10 in Appendices B.2 and B.3) shows the Internal Generated Funds (EbT plus depreciation), equity (including customer contributions, not taken into account in the present analysis) and loan disbursements on the "Source" side. The Application side groups investment and replacement costs, increase in Net Working Capital, tax, interest and repayments. The balance forms the Surplus (Deficit) derived from total operations. Details can be taken from Table 1o in the Appendices cited above.

All major financial statements in current terms (Cash flow, Income and Expenditure Statement and Sources and Application of Fund) clearly indicate that the project is financially in a difficult situation, particularly during the early years of operation. This is the case due to high financial burdens (investments) in the first years and slow revenue generation built-up. Given the recommended tariff structure, overall revenues already cover total outflows as from year 2012 onwards, once investment activities have come to an end, in spite of replacements required for the renewal of major mechanical and electrical equipment. The accumulated surplus finally turns positive in the year 2019 and remains positive during the remaining planning period (see Table 8: Cash Flow in Appendix B.2).

The Net income turns positive as from the year 2014 onwards and stays positive throughout the remaining planning period, while high financial losses in the early years of the project prevent the generation of accumulated net income prior to year 2020, see Table 9: Income and Expenditure Statement in Appendix B.2. In current terms, however, revenues do not suffice to develop a positive accumulated net income, as can be seen from Table 9: Income and Expenditure Statement in Appendix B.3.

Internal generated funds (income before tax and depreciation) in combination with working capital represent sufficient resources as from year 2011 (2013 in current terms) onwards to honour all financial obligations outside of necessary investments required to ensure continuous operations. Corresponding information can be taken from Table 10: Sources and Application of Funds in Appendices B.2 and B.3 in constant and current terms respectively.

Over the period under consideration, the debt service ratio, defined as the relation between Internal Generated Funds and the debt service (repayments plus interest), becomes and stays positive (above the value of 1), in the year 2013. A debt service ratio of below 1 indicates the need for external funding with regard to repayments (and investments, if required).

To overcome difficulties in financial operations resulting there from, particularly with regard to investments, external financing would still be required up to the year 2014 as well as during the years 2015 to 2018 to finance the planned extension of the supply system in the year 2015 and replacements necessary for continued operations during the period of 2016 to 2018.

Excluding taxation on income does not substantially alleviate the situation as the need for additional financial resources in the initial years would not be affected since the enterprise would anyway only become liable for tax once the net income turns positive while the need for external financing during the period 2015 to 2018 would still remain. For details see the corresponding Cash Flow (Table 11), the Income Statement and Expenditure (Table 12) and the Sources and Application of Funds (Table 13) attached to Appendices B2 and B3 respectively may be reviewed.

Table 12.12 Sensitivity Analysis  1)

| Parameter | Constant Terms |  |  | Current terms |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | FIRR (%) | NPV mill € | BC Ratio | FIRR (%) | NPV mill € | BC Ratio |
| Costs + 10 % | 8.3 | -0.40 | 0.90 | 6.7 | -0.91 | 0.83 |
| Revenues + 10 % | 11.4 | 0.33 | 1.09 | 10.0 | 0.00 | 1.00 |
| Costs - 10 % | 11.5 | 0.33 | 1.10 | 10.2 | 0.05 | 1.01 |
| Revenues - 10 % | 8.2 | -0.40 | 0.89 | 6.5 | -0.87 | 0.82 |
| Cost + 10%, revenues -10% | 6.7 | -0.76 | 0.81 | 4.8 | -1.35 | 0.75 |
| Cost - 10%, revenues +10% | 13.1 | 0.69 | 1.21 | 11.9 | 0.49 | 1.11 |
| With tariff increases 2) | 0.2 | -1.61 | 0.54 | -2.5 | -2.26 | 0.56 |

1) Criteria tested is based on opportunity costs of capital of 10%

2) Tariff increases of 1% per year in real terms, that is in addition to inflation, have been assumed

Sensitivity tests based on parameters adhering to common methodological standards as shown in Table 12.12 above prove the project to be fairly robust to variations of major parameters. It shows, however, that either increases in costs as well as reductions in revenues in the order of 10 % show critical results. A combination of both, however, may put the justification for financing at stake, unless lower opportunity costs of capital than 10% could be accepted. Given the social nature of the project, this seems to be feasible.

All parameters tested (FIRR; NPV and Cost/Benefit ratio in addition to the outcome proved by the Cash Flow Analysis) indicate that standards, generally required by internal financing agencies, that is an internal rate of return equivalent to the opportunity costs of capital (here assumed to be 12%) may be achieved in either of the scenarios tested.

But tariff increases as assumed in the present analysis are required to assure above standards. However, given the difficult economic environment in the project region at present, increases for private households, particularly for the lower income brackets beyond rates discussed in Section 12.4.2: Tariff Structure may hardly be acceptable. In order to relieve particularly low-income private households from high water bills, further increases would be justified for the commercial and industrial sector, as mentioned in Section 12.5: Financing above, provided commonly accepted standards would be adhered to.

## Conclusions

Given the undeniable overall advantages an efficient and reliable water supply and sewerage services carries not only for the population but for the region as a whole, in combination with additional social and environmental improvements in the area together with new impetus for commercial and industrial activities in the region, the recommended improved and enlarged water supply and sewerage services must be regarded as indispensable in the long run. Particularly health aspects could become an extra pushing criteria in the near future to accelerate an economic development in the region with large potential for long term sustainability.

The financial analysis indicates that the proposed activities may be recommended for financing, particularly if the Administration concerned, together with the public Head Organisation and the private operator agree on sound managerial (optimised tariff structure) and operational standards. Indeed, if combined with the introduction of still existing additional revenue generation activities (services, extended water supply network and sewerage coverage), the financial viability of the utility would sustain throughout forthcoming operations.

This, however, may include further increases of water charges, particularly for the commercial and most likely industrial sector. However, in particular less well-off private households would hardly be capable to pay higher charges.

APPENDICES

APPENDIX A:	Costs Used in the Economic Analysis

APPENDIX B: 	Financial Analysis

APPENDIX  A: Costs Used in the Economic Analysis

APPENDIX B: Financial Analysis

B.1:	Basic Information

B.2:	Financial Analysis : Constant Terms

B.3:	Financial Analysis : Current Terms

APPENDIX  B.1: Basic Information

Table 1:	Water Demand

Table 2:	Water per User Group

Table 3:	Connections

Table 4:	Water Tariffs

Table 5:	Existing Infrastructure

Table 6:	Rehabilitation Costs

Table 7:	Investment Costs Extension

APPENDIX  B.2: Financial Analysis : Constant Terms

Table 1.1:	Implementation Schedule

Table 1.2:	Investment Schedule

Table 2:	Replacement Costs

Table 3:	Operation & Maintenance

Table 4:	Working Capital

Table 5:	Financing

Table 6:	Dept Service

Table 7:	Revenues

Table 8:	Cash Flow

Table 9:	Income & Expenditure Statement

Table 10:	Sources and Application of Funds

Table 11:	Cash Flow, excluding Income Tax

Table 12:	Income & Expenditure Statement, excluding Income Tax

Table 13:	Sources and Application of Funds, excluding Income Tax

Table 14:	Internal Rate of Return

APPENDIX  B.3: Financial Analysis : Current Terms

Table 1.1:	Implementation Schedule

Table 1.2:	Investment Schedule

Table 2:	Replacement Costs

Table 3:	Operation & Maintenance

Table 4:	Working Capital

Table 5:	Financing

Table 6:	Dept Service

Table 7:	Revenues

Table 8:	Cash Flow

Table 9:	Income & Expenditure Statement

Table 10:	Sources and Application of Funds

Table 11:	Cash Flow, excluding Income Tax

Table 12:	Income & Expenditure Statement, excluding Income Tax

Table 13: 	Sources and Application of Funds, excluding Income Tax

Table 14:	Internal Rate of Return

The household is a group consisting of one or several persons irrespective of the existence of a family tie among them, who live in the same house or a part thereof, eating from the same kitchen, pooling their incomes and expenditures, and participating in the household services and management

The adoption of a particular funding strategy must be related to various factors to which the type of the user of the new facility (public, private), objectives pursued by the operator (single- or multi-purpose), investment-, management- and operation and maintenance costs, financing concept (cost recovery, pricing policies with regard to fees, co-operation models) and the characteristics of the region under consideration are the most important